## README
This excel is a subset of the full IFC-SG mapping, and will be updated as CORENET X tech enablers (Collaboration Platform, Automated Model Checker) are developed
This excel is to be shared with industry practitioners and related partners involved in CORENET X pilots and preparations
Using this excel:
1) | CORENET X Pilot Mapping: This provides details on the identified building component and the associated IFC representations to use
*Important: if IFC-SG Dimension parameter such as “Length, “Breadth” matches the native BIM object’s parameter, there is no need to declare the parameter in project, it will be exported automatically via the configuration files provided
2) | List of Space Parameter Values: Pls refer to the CORENET X Code of Practice (1st Edition) Pg 300 - 343
https://go.gov.sg/cxcop
3) | Please read the change log tab for updates to the mapping
4) | The mapping is WIP, users to note that the mapping is not finalised

## Change Log
Date | Status | Topic | Description
2023-10-20 | Modify | All | Changes to align to the 1st Edition of the CORENET X Code of Practice
2023-07-02 | Modify | All | Changes to align to the Draft Release of the CORENET X Code of Practice
2023-05-12 | Modify | Property and unit | Capacity for Water Meter is changed to WaterUsagePerMonth with Unit m3/month
2023-05-12 | Modify | Unit | Capacity for Sump pump is changed from L to L/s
2023-05-05 | Modify | SubType | DOMESTICCOLDWATER changed to POTABLEWATER
2023-03-29 | Added | Property | Added Property "FireEmergencyVentilationMode" to IfcSpace
2023-03-10 | Modify | Property | URA updates on propertyname to be ACN_IsOpen24HrsToPublic
2023-02-28 | Removed | IP | Removed IP Children Friendly Properties for MEP disciplines for IC Child Urinal
2023-02-27 | Modify | Discipline | Replaced MEP Discipline to ARC for IC Platform lift
2023-02-27 | Modify | IP | IP "Location" term for Wet Riser, Dry Riser, Breeching Inlet, Hosereel, Standby Firehose, and Strobelight are not required as a separate property, thus removed the IP for clarity
2023-02-27 | Removed | Discipline | Removed ARC disciplines for Audio Alarms , ARC does not submit location of detectors & sensors in FSSD
2023-02-27 | Added | IC ,SubType, Property & Properties | URA updates IC : Area Strata Subtype: *AREA_STRATA Property : SGPset_SpaceArea_Strata Properties: AST_AreaType , AST_LegalArea , AST_Extg_StrataLotNumber , AST_Prop_StrataLotNumber, AST_AssociatedTo As per URA new excel (27th Feb Email Exchange)
2023-02-27 | Removed | IC ,SubType, Property & Properties | URA updates IC : Area Unit Subtype: *AREA_UNIT Property & Properties under : SGPset_SpaceArea_Unit As per URA new excel (27th Feb Email Exchange)
2023-02-27 | Modify | SubType | URA Updates - renamed *STRATALOT as per URA requested reps
2023-02-27 | Modify | Properties | Modified URA IC: Area GFA properties As per URA new excel (27th Feb Email Exchange)
2023-02-27 | Modify | Properties | Modified URA IC: Area Connectivity properties As per URA new excel (27th Feb Email Exchange)
2023-02-27 | Modify | Properties | Modified URA IC: Area Landscape properties As per URA new excel (27th Feb Email Exchange)
2023-02-27 | Removed | IC ,SubType, Property & Properties | URA updates: Removed existing specific areas, and to refer to the summary of areas URA has provided, for information to be submitted in the specified structures
2023-02-06 | Removed | IFC Entity | Removed IFC CivilElement for Road Verging, to use ifcSpace with SubTypes
2023-02-02 | Added | Discipline | added water closer, sink, shower, bell, strobelight, standby fire hose, hosereel and breeching inlet into ARC and MEP disciplines
2023-02-02 | Added | Discipline | added smokesensor, firesensor, heat detector, Dry Riser and Wet Riser into ARC and MEP disciplines
2023-02-01 | Added | Properties | added properties ComplyToPUBStandardDrawing and ReferToDrawingNumber
2023-02-01 | Removed | Properties | Grease Trap Length Height Width properties removed as details are in 2D drawings/standard design. PUB is requiring placeholder models to check for clashes with other objects
2023-02-01 | Removed | Properties | Height of Inspection Chamber removed, PUB checks for Depth, Top and invert level
2023-01-31 | Modify | Sandbox Addition | tagged R1 to SCDF PWD Systems (Speakers and Comms Devices and PWD Holding Point)
2023-01-17 | Added | Property | Added Deflection to IfcBeam
2023-01-05 | Modify | Revit Representation | Updated subtype LIFT's Revit Representation to Specialty Equipment
2022-12-23 | Modify | Discipline | Slab with Construction method is changed from ARC to STR domain discipline
2022-12-23 | Modify | Discipline | IC: Bedding disciplines changed from STR to External Works
2022-12-23 | Modify | Discipline | IC: Green Verge discipline changed from ARC to External Works
2022-12-23 | Added | Property | Added IntumescentPaintFireRating and EnclosureFireRating to SCDF Intumescent clause
2022-12-23 | Removed | Property | removed cable segment Fire Rating for clause on protected shaft used for enclosure of services
2022-12-23 | Removed | Property | Removed Fire Rating from IC Below: Cable Fitting Cable Segment Power Power Cable Pump Signal Cable Solar Panel Water Tank Window
2022-12-23 | Modify | IFC-SG Sub Type | IC: Smoke Engineering Air to ENGINEEREDSMOKECONTROLSYSTEM distributionSystem sub type
2022-12-23 | Added | IFC-SG Sub Type | Added system for SCDF SMOKECONTROL, SMOKEPURGING, SMOKEVENT, FIREEXTINGUISHING, FIREHYDRANT, SPRINKLER, HOSEREEL
2022-12-23 | Modify | IFC-SG Sub Type | IC: Sub Alarm Panel subtype ALARMPANEL to SUBALARMPANEL
2022-12-23 | Modify | IFC-SG Sub Type | IC: Main Alarm Panel subtype ALARMPANEL to MAINALARMPANEL
2022-12-23 | Removed | IFC | removed mapping from visual indicator as SCDF noted it is present in control panels, modeller need not model to such details
2022-12-23 | Modify | IFC-SG Sub Type | IC: Visual Alarm subtype updated to USERDEFINED STROBELIGHT
2022-12-21 | Added | Entity | added Accessway, Accessroad, FireEngineAccessway, FireEngineAccessroad, VehicularServiceRoad, Ingress, Egress with representation IfcSpace
2022-12-21 | Modify | Property | re-tag BCA structural requirements
2022-12-21 | Modify | Entity, Propertyset, SubType | modified PUB FOUNDATION from GeographicElement to PipeSegment (Tag to drains)
2022-12-21 | Modify | Domain, Discipline | Property WeldedMesh to be under STR instead of ARC
2022-12-21 | Modify | Domain, Discipline | Property LateralLoad to be under STR instead of ARC
2022-12-21 | Modify | PropertySet | SystemDimension changed to PipeSegmentDimension
2022-12-21 | Modify | IFC-SG Sub Type | subtype GRATING with properties AirTight and WaterTight was changed to INSPECTIONCHAMBERCOVER
2022-12-21 | Modify | IFC-SG Sub Type | IC: DetentionTank subtype STORAGE updated to DETENTIONTANK
2022-12-21 | Modify | Entity | SubType GONDOLA entity changed from BldgSystem to BEP
2022-12-21 | Modify | Property | Aligned IC: Water Tank (Potable Water) to same mapping as Water Tank with isPotable property
2022-12-20 | Modify | Property Set | Updated STR SGPset_Staircase to SGPset_Stair for alignment with ARC requirement
2022-12-20 | Modify | Property | all IP Material has SGPset_Material with property Material now
2022-12-11 | Modify | Property | Precast Stair MechanicalConnectionType label changed to HasMechanicalConnection boolean, ARC to STR discipline
2022-12-11 | Modify | Property Type | Flowrate data type update to Flow
2022-12-11 | Modify | Property Type | capacity data type update to volume
2022-12-08 | Modify | Data Unit | Aligned all Length Data Type to be in Unit "mm"
2022-12-08 | Modify | Property Units | Updated Nparks Girth and Height property unit from meters to mm
2022-12-07 | Removed | Property | URA Property HardscapeType
2022-12-07 | Modify | Property Set | URA SoftscapeType was changed to LandscapeType
2022-12-07 | Modify | Property | Update mapping for URA Area Schemes to refer to URA Excel (Sandbox) for Area Types: LANDSCAPE, CONNECTIVITY, UNIT and GFA
2022-12-05 | Removed | removed from mapping | Sandbox email from magdalene, nparks mentioned no need external planting Changed IC and IP to N.A
2022-12-05 | Modify | IFC-SG Sub Type | SCDF IC: Fire Sensor with object type SMOKEDETECTOR + SmokeDetectorType Property
2022-12-05 | Modify | Property | SCDF IC: Fire Sensor with object type SMOKEDETECTOR + SmokeDetectorType Property
2022-12-02 | Added | Property | IC: Blast Door to have Width and Height
2022-11-11 | Modify | Revit Representation | updated propose revit representation of "Accessway", "Accessroad", "Fire Engine Access Road", "Vehicular Service Road", "Ingress", "Egress" from "Room" to "Areas"
2022-11-07 | Modify | Entity | [Representation Relaxation] Updated Entity for Subtype "GONDOLA" from IfcBuildingSystem to IfcBuildingElementProxy
2022-11-07 | Modify | SubType | Updated IC: DetentionTank Subtype from "STORAGE" to "DETENTION" Removed property "IsPotable" for SubType "DETENTION"
2022-10-27 | Added | General | Added version number (date of modification) to the industry mapping
2022-10-27 | Modify | Properties | Cells in YELLOW for dimension properties to indicate automatic extractive from Native when export to IFC (Modellers no need to create extra dimension parameters for manual input)
2022-10-25 | Added | Object Type | Updated ACESSWAY, ACCESSROAD, FIREENGINEACCESSROAD, FIREENGINEACCESSWAY, VEHICULARSERVCEROAD, INGRESS, EGRESS as object types for IfcSpace, created as alternative representation for roads tagging for multi agencies road verging
2022-09-22 | Added | README Tab | readers to be informed that if dimension parameters (e.g. Length, Breadth) in mapping is the same as the native dimension parameters, there is no need to declare it again in the project, it will be handled via the export configurations
2022-09-22 | Modify | Revit Representation | updated propose revit representation of "Car lot", "Motor Cycle Lot" from "Generic Model" to "Parking"
2022-09-20 | Modify | IFC | Aligned IFC structures for URA GFA, LANDSCAPE, CONNECTIVITY, UNIT for reference to "URA EXCEL"
2022-09-15 | Modify | Property Set | Aligned "SGPset_Staircase" to "SGPset_Stair"
2022-09-15 | Modify | All | Consolidated URA Area Verging requirements into separate file: "URA Excel"
2022-09-08 | Added | Object Type | Added IfcSpace Object types for indication of road plans by multiple agencies, e.g. Accessway, Access Road, Fire Engine Accessway, Fire Engine Access Road, Vehicular Service Road, Ingress and Egress
2022-09-05 | Added | Property | Updated List of STR properties
2022-09-01 | Added | Property | ReferToDrawingNumber to STR members

## Change Details
Agency | Identified Component | Identified parameters | Revit Representation | Archicad Representation | Tekla Structures Representation | Bentley OpenBuildings Representation | Discipline | IFC4 Entities | IFC Sub Types (* = USERDEFINED) | Property Set | Property Name | Property Type | Property Unit | IFC4 Material Set | Sample Value for Reference | Changes from Previous Version
BCA | Accessible Route | Barrier Free Accessibility | Floors | Slab | Slab | Slab | ARC | IfcSlab | *ACCESSIBLEROUTE | SGPset_Slab | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Slab | Bottom Distribution Nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | BottomDistribution_nominal | Label | N.A | N.A | H25-150+H16-300
BCA | Slab | Bottom Main Nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | BottomMain_nominal | Label | N.A | N.A | H25-150+H16-300
BCA | Slab | Construction Method | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Electrical Fixture for Household / Storey Shelter | OutletSocketType | Electrical Fixtures | Object | N.A | Object | MEP | IfcSwitchingDevice | POWEROUTLET | SGPset_SwitchingDevice | OutletSocketType | Label | N.A | N.A | N.A | Multiple Columns C, D, E, G, I, J, K, L, M (Identified Parameters, Revit Representation, Archicad Representation, Bentley OpenBuildings Representation, IFC4 Entities, IFC Sub Types, Property Set, Property Name, Property Type)
LTA | Road | N.A | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Space | Precaster Accreditation Scheme Accreditation | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Household Shelter | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
BCA | Parking Lot | Barrier Free Accessibility | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
BCA | Space | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
BCA | Storey Shelter | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
BCA | Space | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *DRYRISER | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *HOSEREEL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Sprinkler (Non-Fire; for NEA) | N.A | Sprinklers | Terminal | N.A | Sprinkler | MEP | IfcSanitaryTerminal | *SPRINKLER | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Gutter | N.A | Plumbing Fixtures | Pipe | N.A | Drains&Basins | MEP | IfcPipeSegment | GUTTER | N.A | N.A | N.A | N.A | N.A | N.A
NEA | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *PWCSINSPECTIONCHAMBER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | RC Tank | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
PUB | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcBuildingSystem | *DRAINAGE | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Waste Terminal | N.A | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | FLOORTRAP | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Grating | N.A | Generic Models | Covering | N.A | Object | ARC | IfcDiscreteAccessory | *GRATING | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pump | N.A | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
PUB | System | Material | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | SGPset_Material | Material | Label | N.A | Name | N.A | Only Column O (IFC4 Material Set)
PUB | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
PUB | Water Closet | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | *WATERCLOSET | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Water Closet | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | *WATERCLOSET | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Water Closet | Ambulant Disabled | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | AmbulantDisabled | Boolean | N.A | N.A | TRUE/FALSE
BCA | Water Closet | Barrier Free Accessibility | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
NEA | Water Closet | Children Friendly | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE
PUB | Tank | Trade Effluent | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *BALANCINGTANK | SGPset_Tank | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *FIREALARMPANEL | N.A | N.A | N.A | N.A | N.A | N.A | Only Column J (IFC Sub Types)
SCDF | Breeching Inlet | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | ARC | IfcFireSuppressionTerminal | BREECHINGINLET | N.A | N.A | N.A | N.A | N.A | N.A
PUB | System | Length | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A
SCDF | Security Lighting | N.A | Lighting Fixtures | Object | N.A | Object | MEP | IfcLightFixture | SECURITYLIGHTING | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Space | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
NEA | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *RAINWATER | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
SCDF | Sensor | N.A | Fire Alarm Devices | Object | N.A | Solid | ARC | IfcSensor | *FLAMEDETECTOR | N.A | N.A | N.A | N.A | N.A | N.A | Removed
SCDF | Sensor | N.A | Fire Alarm Devices | Object | N.A | Solid | ARC | IfcSensor | *HEATDETECTOR | N.A | N.A | N.A | N.A | N.A | N.A | Removed
SCDF | Sensor | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcSensor | *HEATDETECTOR | N.A | N.A | N.A | N.A | N.A | N.A | Removed
SCDF | Hose Reel | N.A | Mechanical Equipment | Pipe Flow Terminal | N.A | Fixture | ARC | IfcFireSuppressionTerminal | HOSEREEL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *LANDINGVALVE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Pump | N.A | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
PUB | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Sensor | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcSensor | *SMOKEDETECTOR | N.A | SmokeDetectorType | Label | N.A | N.A | N.A | Removed
PUB | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
PUB | System | Gradient | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | SGPset_PipeSegmentDimension | Gradient | Label | N.A | N.A | N.A
PUB | System | Length | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A
SCDF | Hose Reel | N.A | Mechanical Equipment | Pipe | N.A | Pipe | ARC | IfcFireSuppressionTerminal | *STANDBYFIREHOSE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | ARC | IfcAlarm | *MANUALALARMCALLPOINT | N.A | N.A | N.A | N.A | N.A | N.A | Only Column J (IFC Sub Types)
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *VISUALALARM | N.A | N.A | N.A | N.A | N.A | N.A | Only Column J (IFC Sub Types)
PUB | Tank | Nominal Capacity | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | Pset_TankTypeCommon | NominalCapacity | Volume | L | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SMOKECONTROL | N.A | N.A | N.A | N.A | N.A | N.A
URA | Window | Operation Type | Windows | Window | N.A | Window | ARC | IfcWindow | *BAYWINDOW | SGPset_Window | OperationType | Label | N.A | N.A | N.A | Multiple Columns C, K, L, M (Identified Parameters, Property Set, Property Name, Property Type)
URA | Building Element | N.A | N.A | N.A | N.A | N.A | ARC | IfcElement | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Building Storey | N.A | Levels | Storey | N.A | Floor | ARC | IfcBuildingStorey | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Control Panel | N.A | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | CONTROLPANEL | N.A | N.A | N.A | N.A | N.A | N.A
URA | Electrical Equipment - Electric Flow Storage Device | N.A | Electrical Equipment | Object | N.A | Equipment | MEP | IfcElectricFlowStorageDevice | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A | Removed
URA | Gondola | N.A | Massing | Morph | N.A | Forms | ARC | IfcBuildingElementProxy | *GONDOLA | N.A | N.A | N.A | N.A | N.A | N.A
URA | Mechanical Equipment - Chiller | N.A | Mechanical Equipment | Object | N.A | Mechanical Equipment | MEP | IfcChiller | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Pump | N.A | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Mechanical Equipment - Unitary Equipment | N.A | Mechanical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryEquipment | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Site Boundary | N.A | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *CADASTRALLOT | N.A | N.A | N.A | N.A | N.A | N.A
URA | Planter Box | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *PLANTERBOX | N.A | N.A | N.A | N.A | N.A | N.A
URA | Roof | N.A | Roofs | Roof | N.A | Roof | ARC | IfcRoof | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Site Boundary | N.A | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *CADASTRALLOT | N.A | N.A | N.A | N.A | N.A | N.A
NPARKS | Site Boundary | Approved Soil Mixture | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *CADASTRALLOT | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
NEA | Water Closet | Pan Mounting | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | PanMounting | Label | N.A | N.A | N.A
BCA | Family-Friendly Furniture | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *CHANGINGBED | N.A | N.A | N.A | N.A | N.A | N.A | Only Column B (Identified Component)
NEA | Water Closet | Toilet Pan Type | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | ToiletPanType | Label | N.A | N.A | N.A
NParks | Culvert | N.A | Generic Models | Object | Slab, Panel | Drains&Basins | ARC | IfcCivilElement | *ENTRANCECULVERT | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | N.A | Doors | Door | N.A | Door | ARC | IfcDoor | *ACCESSHATCH | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Blast Door | Opening Height | Doors | Door | N.A | Door | ARC | IfcDoor | *BLASTDOOR | SGPset_DoorDimension | OpeningHeight | Length | mm | N.A | N.A | Only Column B (Identified Component)
BCA | Blast Door | Opening Width | Doors | Door | N.A | Door | ARC | IfcDoor | *BLASTDOOR | SGPset_DoorDimension | OpeningWidth | Length | mm | N.A | N.A | Only Column B (Identified Component)
BCA | Blast Door | Operation Type | Doors | Door | N.A | Door | ARC | IfcDoor | *BLASTDOOR | SGPset_Door | OperationType | Label | N.A | N.A | N.A | Multiple Columns C, K, L, M, N (Identified Parameters, Property Set, Property Name, Property Type, Property Unit)
BCA | Lift | N.A | Mechanical Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | ESCALATOR | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *SOUNDER | N.A | N.A | N.A | N.A | N.A | N.A | Only Column J (IFC Sub Types)
SCDF | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *SPRINKLERCONTROL | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | DOUBLECHECK | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | MIXING | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *REFLUXVALVE | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *AIRADMITTANCE | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *DRAINOFFCOCK | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | CHECK | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | ISOLATING | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Lift | N.A | Mechanical Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *GOODSLIFT | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Lift | N.A | Mechanical Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *BINLIFTER | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Balustrade | N.A | Railings | Railing | Component | Railing | STR | IfcRailing | BALUSTRADE | N.A | N.A | N.A | N.A | N.A | N.A
URA | Bollard | N.A | Railings | Railing | Component | Railing | STR | IfcRailing | *BOLLARD | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Footpath | Material | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *FOOTPATH | SGPset_Material | Material | Label | N.A | Name | N.A | Multiple Columns C, K, L, M, O (Identified Parameters, Property Set, Property Name, Property Type, IFC4 Material Set)
SCDF | Sensor | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcSensor | FIRESENSOR | N.A | N.A | N.A | N.A | N.A | N.A | Removed
SCDF | Sensor | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcSensor | GASSENSOR | N.A | N.A | N.A | N.A | N.A | N.A | Removed
SCDF | Sensor | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcSensor | MOVEMENTSENSOR | N.A | N.A | N.A | N.A | N.A | N.A | Removed
SCDF | Sensor | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcSensor | TEMPERATURESENSOR | N.A | N.A | N.A | N.A | N.A | N.A | Removed
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SMOKEPURGING | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | Is Potable | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_Tank | IsPotable | Boolean | N.A | N.A | TRUE/FALSE
PUB | Tank | Height | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_TankDimension | Height | Length | mm | N.A | N.A
PUB | Tank | Length | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_TankDimension | Length | Length | mm | N.A | N.A
PUB | Tank | Width | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_TankDimension | Width | Length | mm | N.A | N.A
BCA | Window | N.A | Windows | Window | N.A | Window | ARC | IfcWindow | SKYLIGHT | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Parking Lot | Bicycle Lot Count | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxy | BicycleLotCount | Integer | N.A | N.A | Limited to 1 or 2 only | Only Column P (Sample Value for Reference)
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *PWCSMANHOLE | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *SAMPLINGSUMP | SGPset_DistributionChamberElement | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE | New
SCDF | Control Element | N.A | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | *AUTOMATICRESCUEDEVICE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Control Element | N.A | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | *LIFTSUPERVISORYPANEL | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Soffit | Fire Rating | Roofs | Roof | N.A | Roof | ARC | IfcCovering | *SOFFIT | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | N.A | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEACCESSPANEL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | Pset_DoorCommon | FireRating | Label | hr | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Air Tight | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | SGPset_Door | AirTight | Boolean | N.A | N.A | TRUE/FALSE
PUB | Water Meter | Purpose | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | Purpose | Label | N.A | N.A | PRIVATE
PUB | Water Meter | Unit Number | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | UnitNumber | Label | N.A | N.A | N.A
PUB | Water Meter | Unit Number Tag | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | UnitNumberTag | Boolean | N.A | N.A | TRUE/FALSE
PUB | Water Meter | Water Supply Source | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | WaterSupplySource | Label | N.A | N.A | N.A
BCA | Chair | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | CHAIR | N.A | N.A | N.A | N.A | N.A | N.A | Multiple Columns B, C, J, K, L, M, P (Identifed Component, Identified Parameters, IFC Sub Types, Property Set, Property Name, Property Type, Sample Value for Reference )
URA | Site | Total Area | Topography | Mesh | N.A | Mesh | ARC | IfcSite | Need not specify | Pset_SiteCommon | TotalArea | Area | m2 | N.A | N.A
SCDF | Staircase | Fire Exit | Stairs | Stair | Component | Stair | ARC | IfcStair | Need not specify | Pset_StairCommon | FireExit | Boolean | N.A | N.A | TRUE/FALSE
BCA | Staircase | Riser Count | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | NumberOfRisers | Integer | N.A | N.A | N.A | Only Column L (Property Name)
BCA | Staircase | Riser Height | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | RiserHeight | Length | mm | N.A | N.A
BCA | Staircase | Tread Width | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | TreadLength | Length | mm | N.A | N.A
SCDF | Staircase | Riser Height | Stairs | Stair | Item | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | RiserHeight | Length | mm | N.A | N.A
SCDF | Staircase | Tread Length | Stairs | Stair | Item | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | TreadLength | Length | mm | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *EJECTORTANK | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *IRRIGATIONTANK | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Tank | Nominal Capacity | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *POTABLEWATER | Pset_TankTypeCommon | NominalCapacity | Volume | L | N.A | N.A
PUB | Tank | Diameter | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *POTABLEWATER | SGPset_TankDimension | Diameter | Length | mm | N.A | N.A
BCA | Wall | Construction Method | Walls | Wall | Panel | Wall | ARC | IfcWall | Need not specify | SGPset_Wall | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Beam | Beam Span Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | BeamSpanType | Label | N.A | N.A | Single, End, Interior, Cantilever
BCA | Beam | Construction Method | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Beam | Construction Method | Structural Framing | Beam | Beam | Beam | ARC | IfcBeam | Need not specify | SGPset_Beam | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Beam | ReferTo2DDetail | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Beam | Reinforcement Steel Grade | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Beam | Section Fabrication Method | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | SectionFabricationMethod | Label | N.A | N.A | Hot rolled, Cold formed
BCA | Beam | Depth | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | Depth | Length | mm | N.A | 600
BCA | Beam | Mark | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | Mark | Label | N.A | N.A | HB1, VB1, B1
BCA | Beam | Member Section | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | MemberSection | Label | N.A | N.A | RHS600x30x4, CHS500x3.0, 254x254x63 kg/m
BCA | Beam | Width | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | Width | Length | mm | N.A | 300
BCA | Beam | Bottom Left | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BottomLeft | Label | N.A | N.A | 3H25
BCA | Beam | Bottom Middle | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BottomMiddle | Label | N.A | N.A | 3H32+3H25+3H20
BCA | Beam | Bottom Right | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BottomRight | Label | N.A | N.A | 3H25
BCA | Beam | Stirrups Left | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsLeft | Label | N.A | N.A | 4H13-300
BCA | Beam | Side Bar | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | SideBar | Label | N.A | N.A | H13-250 | Only Column P (Sample Value for Reference)
BCA | Beam | Stirrups Middle | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsMiddle | Label | N.A | N.A | 4H13-300
BCA | Beam | Stirrups Right | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsRight | Label | N.A | N.A | 4H13-300
BCA | Beam | Top Left | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | TopLeft | Label | N.A | N.A | 3H32+3H25
BCA | Beam | Top Middle | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | TopMiddle | Label | N.A | N.A | 3H25
BCA | Beam | Top Right | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | TopRight | Label | N.A | N.A | 3H32+3H25
BCA | Beam | Stirrups Type Left | Structural Framing | Beam | Concrete Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsTypeLeft | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion | Only Column P (Sample Value for Reference)
BCA | Beam | Stirrups Type Middle | Structural Framing | Beam | Concrete Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsTypeMiddle | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion | Only Column P (Sample Value for Reference)
BCA | Beam | Stirrups Type Right | Structural Framing | Beam | Concrete Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsTypeRight | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion | Only Column P (Sample Value for Reference)
URA | Building | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Factory | Removed
URA | Building | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | N.A
URA | Chalet | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Holiday Resort | Removed
URA | Childcare Centre | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Children’S Home | Removed
URA | Civic and Community Institution | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Civic and Community Institution, Sports and Recreation | Removed
URA | Commercial | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Commercial 1 | Removed
URA | Commercial | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Commercial 2 | Removed
URA | Commercial | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Security office | Removed
URA | Community Centre | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Community Centre | Removed
URA | Hotel | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Hotel | Removed
URA | Independent Workers' Dormitory | Number of Workers | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | NumberOfWorkers | Integer | N.A | N.A | N.A
URA | Kindergarten | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Kindergarten/Nursery | Removed
URA | Office | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Office | Removed
URA | Recreational Facility | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Cultural Institutions | Removed
URA | Residential | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Other residential | Removed
URA | Restaurant | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Restaurant | Removed
URA | Serviced Apartment | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Serviced Apartment | Removed
URA | Showroom | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Showroom | Removed
BCA | Accessible Route | Barrier Free Accessibility | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSIBLEROUTE | SGPset_BuildingElementProxy | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Car Parking Served By Car Lift | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | CarParking_ServedByCarLift | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | EV Lot | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | EVLot | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Bicycle Lot Count | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLERACK | SGPset_BuildingElementProxy | BicycleLotCount | Integer | N.A | N.A | N.A
LTA | Parking Lot | Bicycle Parking Rack Type | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLERACK | SGPset_BuildingElementProxy | BicycleParkingRack_Type | Label | N.A | N.A | Single Tier, Double Tier
BCA | Parking Lot | Family Parking Lot | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | Family Lot | Boolean | N.A | N.A | TRUE/FALSE | Only Column L (Property Name)
BCA | Parking Lot | Length | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
SCDF | Fire Extinguisher | Fire Extinguisher Rating | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *PORTABLEFIREEXTINGUISHER | SGPset_BuildingElementProxy | FireExtinguisherRating | Label | N.A | N.A | 70B
SCDF | Road | Loading Capacity | Areas | Zone | N.A | Space | ARC | IfcBuildingElementProxy | *FIREENGINEACCESSWAY | SGPset_BuildingElementProxy | LoadingCapacity | Real | Tonnes | N.A | 24 tonnes
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
SCDF | Signage | Mounting Height | Specialty Equipment | Object | N.A | Object | ARC | IfcBuildingElementProxy | *SIGNAGE_EXIT | SGPset_BuildingElementProxy | MountingHeight | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Lot Number | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | LotNumber | Label | N.A | N.A | N.A
LTA | Parking Lot | N.A | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Parking Lot | N.A | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BUSLOT | N.A | N.A | N.A | N.A | N.A | N.A
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
BCA | Borehole | Depth | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | Depth | Length | mm | N.A | 14560
LTA | Parking Lot | Parking Use | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | ParkingUse | Label | N.A | N.A | Electric Vehicle, Oil Tanker, Buggy, Vacuum Truck, Mobile Tanker
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Vehicle Type | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | VehicleType | Label | N.A | N.A | Rigid-framed vehicle
BCA | Borehole | Mark | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | Mark | Label | N.A | N.A | BH1
BCA | Borehole | SHD Level SPT MoreThan 100N | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | SHDLevel_SPT_MoreThan_100N | Real | m | N.A | -27.5 | Only Column C (Identified Parameters)
BCA | Borehole | SHD Level SPT MoreThan 60N | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | SHDLevel_SPT_MoreThan_60N | Real | m | N.A | -15 | Only Column C (Identified Parameters)
BCA | Borehole | Termination Level | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | TerminationLevel | Real | m | N.A | -50.45
BCA | Borehole | Top Level | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | TopLevel | Real | m | N.A | 1.8
BCA | Accessible Route | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSIBLEROUTE | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
BCA | Parking Lot | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
URA | Attic Level | Attic Level | Levels | Storey | N.A | Floor | ARC | IfcBuildingStorey | Need not specify | SGPset_BuildingStorey | AtticLevel | Boolean | N.A | N.A | TRUE/FALSE | Multiple Columns B, C, L (Identified Component, Identified Parameters, Property Name)
BCA | Refuse Chute / Recyclables Chute | Construction Method | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *REFUSECHUTE | SGPset_BuildingSystem | ConstructionMethod | Label | N.A | N.A | Prefabricated, Precast, Cast in-situ, Install on-site
BCA | Refuse Chute / Recyclables Chute | Outer Dimensions | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *REFUSECHUTE | SGPset_BuildingSystemDimension | OuterDimensions | Length | mm | N.A | N.A
BCA | Refuse Chute / Recyclables Chute | Inner Dimensions | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *REFUSECHUTE | SGPset_BuildingSystemDimension | InnerDimensions | Length | mm | N.A | N.A
BCA | Refuse Chute / Recyclables Chute | Chamfer Radius | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *REFUSECHUTE | SGPset_BuildingSystemDimension | ChamferRadius | Length | mm | N.A | N.A
PUB | Gutter | Construction Method | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElement | ConstructionMethod | Label | N.A | N.A | N.A
LTA | Road | Ingress | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_CivilElement | Egress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Culvert | Footpath | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | CULVERT | SGPset_CivilElement | Footpath | Boolean | N.A | N.A | TRUE/FALSE
LTA | Road | Egress | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_CivilElement | Ingress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Road | Kerb Type | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_CivilElement | KerbType | Label | N.A | N.A | N.A
LTA | Culvert | Load Bearing | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | CULVERT | SGPset_CivilElement | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Public | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElement | Public | Boolean | N.A | N.A | TRUE/FALSE
PUB | Gutter | Public | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElement | Public | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Diameter | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Culvert | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Gutter | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Culvert | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Gutter | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Culvert | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Gutter | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
LTA | Road | Thickness | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Culvert | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
PUB | Gutter | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
BCA | Column | Construction Method | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Column | Construction Method | Columns | Column | Concrete Column | Column | ARC | IfcColumn | Need not specify | SGPset_Column | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Column | ReferTo2DDetail | Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Column | Reinforcement Steel Grade | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Column | Section Fabrication Method | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | SectionFabricationMethod | Label | N.A | N.A | Hot rolled, Cold formed
BCA | Column | Breadth | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Breadth | Length | mm | N.A | 300
BCA | Column | Diameter | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Diameter | Length | mm | N.A | 600
BCA | Column | End Storey | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | EndStorey | Label | N.A | N.A | 2nd Storey, Roof Storey
BCA | Column | Mark | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Mark | Label | N.A | N.A | TC1, C1
BCA | Column | Member Section | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | MemberSection | Label | N.A | N.A | RHS600x30x4, CHS500x3.0, 254x254x63 kg/m
BCA | Column | Starting Storey | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | StartingStorey | Label | N.A | N.A | 1st Storey, Lower Roof Storey
BCA | Column | Width | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Width | Length | mm | N.A | 600
BCA | Column | Stirrups | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | Stirrups | Label | N.A | N.A | 4H13-300
BCA | Column | Stirrups Type | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion | Only Column P (Sample Value for Reference)
BCA | Column | Main Rebar | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | MainRebar | Label | N.A | N.A | 6H32+6H25
BCA | Column | Working Load DA1-1 | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnStructuralLoad | WorkingLoad_DA1-1 | Integer | kN | N.A | 1234
BCA | Column | Working Load DA1-2 | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnStructuralLoad | WorkingLoad_DA1-2 | Integer | kN | N.A | 1234
SCDF | Damper | Fire Rating | Duct Accessories | Object | N.A | Object | MEP | IfcDamper | FIREDAMPER | SGPset_Damper | FireRating | Label | hr | N.A | 30min, 60min, 90min, 120min, 150min, 180min, 210min, 240min | Only Column P (Sample Value for Reference)
SCDF | Damper | Fire Rating | Duct Accessories | Object | N.A | Object | MEP | IfcDamper | FIRESMOKEDAMPER | SGPset_Damper | FireRating | Label | hr | N.A | 30min, 60min, 90min, 120min, 150min, 180min, 210min, 240min | Multiple Columns C, L, M, N, P (Identified Parameters, Property Name, Property Type, Property Unit, Sample Value for Reference)
SCDF | Damper | Fire Rating | Duct Accessories | Object | N.A | Object | MEP | IfcDamper | SMOKEDAMPER | SGPset_Damper | FireRating | Label | hr | N.A | 30min, 60min, 90min, 120min, 150min, 180min, 210min, 240min | Multiple Columns C, L, M, N, P (Identified Parameters, Property Name, Property Type, Property Unit, Sample Value for Reference)
PUB | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *SCREENCHAMBER | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Distribution Chamber | Depth | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Depth | Length | mm | N.A | N.A
PUB | Distribution Chamber | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Distribution Chamber | Height | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Height | Length | mm | N.A | N.A
PUB | Distribution Chamber | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Length | Length | mm | N.A | N.A
PUB | Distribution Chamber | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Width | Length | mm | N.A | N.A
PUB | Distribution Chamber | Material | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_Material | Material | Label | N.A | Name | N.A | New
PUB | Distribution Chamber | Depth | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | Depth | Length | mm | N.A | N.A
PUB | Distribution Chamber | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Distribution Chamber | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | METERCHAMBER | N.A | N.A | N.A | N.A | N.A | N.A | New
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Distribution Chamber | Depth | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Depth | Length | mm | N.A | N.A
PUB | Distribution Chamber | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Diameter | Length | mm | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Self Closing | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | SGPset_Door | SelfClosing | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | Volume Controlled | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | SGPset_Door | VolumeControlled | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | N.A | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEACCESSPANEL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | Pset_DoorCommon | FireRating | Label | hr | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Air Tight | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | SGPset_Door | AirTight | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | Self Closing | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | SGPset_Door | SelfClosing | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | Volume Controlled | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | SGPset_Door | VolumeControlled | Boolean | N.A | N.A | TRUE/FALSE
LTA | Gate | N.A | Doors | Door | N.A | Door | ARC | IfcDoor | GATE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Door | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | Pset_DoorCommon | FireRating | Label | hr | N.A | N.A
SCDF | Door | Operation Type | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | OperationType | Label | N.A | N.A | N.A
SCDF | Door | Self Closing | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | SelfClosing | Boolean | N.A | N.A | TRUE/FALSE
BCA | Door | Vision Panel | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | VisionPanel | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | Clear Height | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | ClearHeight | Length | mm | N.A | N.A
SCDF | Door | Clear Width | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | ClearWidth | Length | mm | N.A | N.A
BCA | Door | Overall Width | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | OverallWidth | Length | mm | N.A | N.A
BCA | Door | StructuralHeight | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | StructuralHeight | Length | mm | N.A | N.A
BCA | Door | StructuralWidth | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | StructuralWidth | Length | mm | N.A | N.A
SCDF | Breeching Inlet | Hose Nominal Diameter | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | MEP | IfcFireSuppressionTerminal | BREECHINGINLET | SGPset_FireSuppressionTerminal | Hose_NominalDiameter | Label | N.A | N.A | N.A
SCDF | Hose Reel | Hose Nominal Diameter | Mechanical Equipment | Pipe Flow Terminal | N.A | Fixture | MEP | IfcFireSuppressionTerminal | HOSEREEL | SGPset_FireSuppressionTerminal | Hose_NominalDiameter | Label | mm | N.A | N.A
SCDF | Hose Reel | Hose Nominal Diameter | Mechanical Equipment | Pipe | N.A | Pipe | MEP | IfcFireSuppressionTerminal | *STANDBYFIREHOSE | SGPset_FireSuppressionTerminal | Hose_NominalDiameter | Label | mm | N.A | N.A
SCDF | Breeching Inlet | ID | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | MEP | IfcFireSuppressionTerminal | BREECHINGINLET | SGPset_FireSuppressionTerminal | ID | Label | N.A | N.A | N.A
SCDF | Fire Hydrant | ID | Plumbing Fixtures | Object | N.A | Fire Protection | MEP | IfcFireSuppressionTerminal | FIREHYDRANT | SGPset_FireSuppressionTerminal | ID | Label | N.A | N.A | N.A
SCDF | Fire Hydrant | Private | Plumbing Fixtures | Object | N.A | Fire Protection | MEP | IfcFireSuppressionTerminal | FIREHYDRANT | SGPset_FireSuppressionTerminal | Private | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Fire Hydrant | Public | Plumbing Fixtures | Object | N.A | Fire Protection | MEP | IfcFireSuppressionTerminal | FIREHYDRANT | SGPset_FireSuppressionTerminal | Public | Boolean | N.A | N.A | TRUE/FALSE
PUB | Water Meter | Capacity | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | SGPset_FlowMeter | Capacity | Volume | L/s | N.A | N.A | Multiple Columns M, N (Property Type, Property Unit)
PUB | Water Meter | Diameter | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | SGPset_FlowMeterDimension | Diameter | Length | mm | N.A | N.A
PUB | Water Meter | Length | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | SGPset_FlowMeterDimension | Length | Length | mm | N.A | N.A
BCA | Footing | DA1-1 Bearing Capacity | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | DA1-1_BearingCapacity | Integer | kPa | N.A | 150 | Only Column P (Sample Value for Reference)
BCA | Footing | DA1-2 Bearing Capacity | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | DA1-2_BearingCapacity | Integer | kPa | N.A | 120 | Only Column P (Sample Value for Reference)
BCA | Footing | ReferTo2DDetail | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Footing | Reinforcement Steel Grade | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Footing | Soil Verification Test | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | SoilVerificationTest | Label | N.A | N.A | 2 nos plate load Test
BCA | Footing | Breadth | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Breadth | Length | mm | N.A | 6200
BCA | Footing | Depth | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Depth | Length | mm | N.A | 300
BCA | Footing | Mark | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Mark | Label | N.A | N.A | F2, PC1, PC2, PC4_1
BCA | Footing | Width | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Width | Length | mm | N.A | 300
BCA | Footing | Side Bar | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | SideBar | Label | N.A | N.A | H13-250
BCA | Footing | Stirrups | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | Stirrups | Label | N.A | N.A | H13-200-300
BCA | Footing | Stirrups Type | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion | Only Column P (Sample Value for Reference)
BCA | Footing | Top Distribution | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | TopDistribution | Label | N.A | N.A | H16-150
BCA | Footing | Bottom Distribution | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | BottomDistribution | Label | N.A | N.A | H16-150
BCA | Footing | Bottom Main | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | BottomMain | Label | N.A | N.A | H25-150
BCA | Footing | Top Main | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | TopMain | Label | N.A | N.A | H25-150
BCA | Footing | Working Load DA1-1 | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FoundationStructuralLoad | WorkingLoad_DA1-1 | Integer | kN | N.A | 4321 | Multiple Columns C, L (Identified Parameters, Property Name)
BCA | Cubicle | Barrier Free Accessibility | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *CUBICLE | SGPset_Furniture | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Cubicle | Ambulant Disabled | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *CUBICLE | SGPset_Furniture | AmbulantDisabled | Boolean | N.A | N.A | TRUE/FALSE
NEA | Bench | Capacity | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *BENCH | SGPset_Furniture | Capacity | Label | N.A | N.A | N.A
NPARKS | Site Boundary | Area | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *CADASTRALLOT | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
NPARKS | Green Verge | Approved Soil Mixture | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Green Verge | Shrubs | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | Shrubs | Label | N.A | N.A | N.A | Multiple Columns C, L (Identified Parameters, Property Name)
NPARKS | Green Verge | Area | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
NPARKS | Landscape Plants | Approved Soil Mixture | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_EXTERNALPLANTING | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Landscape Plants | Girth | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElementDimension | Girth | Length | mm | N.A | N.A
NPARKS | Landscape Plants | Girth | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElementDimension | Girth | Length | mm | N.A | N.A
NPARKS | Landscape Plants | Palm Type | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | PalmType | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Reason For Removal | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | ReasonForRemoval | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Single Stem | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | SingleStem | Boolean | N.A | N.A | TRUE/FALSE | Only Column P (Sample Value for Reference)
NPARKS | Landscape Plants | Single Stem | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | SingleStem | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Landscape Plants | Species | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_HEDGE | SGPset_GeographicElement | Species | Label | N.A | N.A | N.A | Removed
NPARKS | Landscape Plants | Species | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | Species | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Species | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_SHRUBS | SGPset_GeographicElement | Species | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Species | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | Species | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Status | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | Status | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Status | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_SHRUBS | SGPset_GeographicElement | Status | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Status | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | Status | Label | N.A | N.A | To be retained, To be felled/removed, To be transplanted, To be planted/proposed/new
NPARKS | Landscape Plants | Height | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElementDimension | Height | Label | N.A | N.A | N.A | Multiple Columns C, L (Identified Parameters, Property Name)
NPARKS | Landscape Plants | Tree Number | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | TreeNumber | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Tree Size | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | TreeSize | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Tree Size | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | TreeSize | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Turf | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_SHRUBS | SGPset_GeographicElement | Turf | Boolean | N.A | N.A | TRUE/FALSE
URA | Neighbouring Lot | N.A | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *NEIGHBOURINGLOT | N.A | N.A | N.A | N.A | N.A | N.A
NPARKS | Planting Area | Approved Soil Mixture | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
URA | Soil | Approved Soil Mixture | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Carpark Provision | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | CarparkProvision | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Compensated | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | Compensated | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Status | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | Status | Label | N.A | N.A | N.A
NPARKS | Planting Area | Turf | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | Turf | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Turf Species | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | TurfSpecies | Label | N.A | N.A | N.A
NPARKS | Planting Area | Area | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
PUB | Interceptor | Comply to PUB Standard Drawing | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_Interceptor | ComplyToPUBStandardDrawing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Interceptor | Comply to PUB Standard Drawing | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_Interceptor | ComplyToPUBStandardDrawing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Interceptor | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Diameter | Length | N.A | N.A | N.A
PUB | Interceptor | Height | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Height | Length | N.A | N.A | N.A
PUB | Interceptor | Height | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | Height | Length | N.A | N.A | N.A
PUB | Interceptor | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Length | Length | N.A | N.A | N.A
PUB | Interceptor | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | Length | Length | N.A | N.A | N.A
PUB | Interceptor | Refer to Drawing Number | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_Interceptor | ReferToDrawingNumber | Label | N.A | N.A | N.A
PUB | Interceptor | Refer to Drawing Number | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_Interceptor | ReferToDrawingNumber | Label | N.A | N.A | N.A
PUB | Interceptor | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Width | Length | N.A | N.A | N.A
PUB | Interceptor | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | Width | Length | N.A | N.A | N.A
BCA | Beam | Material Grade | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete | Multiple Columns O, P (IFC4 Material Set, Sample Value for Reference)
BCA | Pile | Borehole Ref | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | BoreholeRef | Label | N.A | N.A | BH2, BH3, BH12-2
BCA | Column | Material Grade | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete | Multiple Columns O, P (IFC4 Material Set, Sample Value for Reference)
BCA | Wall | Construction Method | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
SCDF | Wall | Fire Rating | Walls | Wall | Panel | Wall | ARC | IfcWall | Need not specify | Pset_WallCommon | FireRating | Label | hr | N.A | N.A
BCA | Railing | Material | Railings | Railing | Component | Railing | STR | IfcRailing | GUARDRAIL | SGPset_Material | Material | Label | N.A | Name | N.A | Only Column M (Property Type)
BCA | Wall | Horizontal Rebar | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | HorizontalRebar | Label | N.A | N.A | H20-150
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SMOKEVENT | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Staircase | Material Grade | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete | Multiple Columns O, P (IFC4 Material Set, Sample Value for Reference)
BCA | Footing | Material Grade | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete | Multiple Columns O, P (IFC4 Material Set, Sample Value for Reference)
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | FLOORTRAP | SGPset_Material | Material | Label | N.A | Name | N.A | Only Column O (IFC4 Material Set)
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | FLOORWASTE | SGPset_Material | Material | Label | N.A | Name | N.A | Multiple Columns C, O (Identified Parameters, IFC4 Material Set)
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | GULLYSUMP | SGPset_Material | Material | Label | N.A | Name | N.A | Multiple Columns C, O (Identified Parameters, IFC4 Material Set)
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | GULLYTRAP | SGPset_Material | Material | Label | N.A | Name | N.A | Multiple Columns C, O (Identified Parameters, IFC4 Material Set)
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | WASTETRAP | SGPset_Material | Material | Label | N.A | Name | N.A | Multiple Columns C, O (Identified Parameters, IFC4 Material Set)
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | *WASTESUMP | SGPset_Material | Material | Label | N.A | Name | N.A | Multiple Columns C, O (Identified Parameters, IFC4 Material Set)
BCA | Pile | Breadth | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Breadth | Length | mm | N.A | 300
BCA | Pile | Construction Method | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC, Spun
BCA | Pile | CutOffLevel_SHD | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | CutOffLevel_SHD | Real | m | N.A | -1.35
BCA | Pile | DA1-1 Compression Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-1_CompressionCapacity | Integer | kN | N.A | 5683
BCA | Pile | DA1-1 Compression Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-1_CompressionDesignLoad | Integer | kN | N.A | 5515
BCA | Pile | DA1-1 Tension Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-1_TensionCapacity | Integer | kN | N.A | 3655
BCA | Pile | DA1-1 Tension Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-1_TensionDesignLoad | Integer | kN | N.A | 3255
BCA | Pile | DA1-2 Compression Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-2_CompressionCapacity | Integer | kN | N.A | 4823
BCA | Pile | DA1-2 Compression Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-2_CompressionDesignLoad | Integer | kN | N.A | 4650
BCA | Pile | DA1-2 Tension Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-2_TensionCapacity | Integer | kN | N.A | 3025
BCA | Pile | DA1-2 Tension Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-2_TensionDesignLoad | Integer | kN | N.A | 2850
BCA | Pile | Diameter | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Diameter | Length | mm | N.A | 600
BCA | Pile | Length | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Length | Length | mm | N.A | 40000
BCA | Pile | Main Rebar | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | MainRebar | Label | N.A | N.A | 10H32+10H16
BCA | Pile | Mark | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Mark | Label | N.A | N.A | P156
BCA | Pile | Material Grade | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete | Multiple Columns O, P (IFC4 Material Set, Sample Value for Reference)
BCA | Pile | Member Section | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | MemberSection | Label | N.A | N.A | CHS500x3.0, 254x254x63 kg/m
BCA | Pile | Min Embedment Into Bearing Layer SPT More Than 100 N | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | MinEmbedmentIntoBearingLayer_SPT_MoreThan_100N | Real | m | N.A | 16.5
BCA | Pile | Min Embedment Into Bearing Layer SPT More Than 60 N | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | MinEmbedmentIntoBearingLayer_SPT_MoreThan_60N | Real | m | N.A | 23.2
BCA | Pile | Min Rock Socketing Length | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | MinRockSocketingLength | Real | m | N.A | 16.5
BCA | Pile | Negative Skin Friction | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | NegativeSkinFriction | Integer | kN | N.A | 135
BCA | Pile | Pile Type | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | PileType | Label | N.A | N.A | Driven, Bored, Jacked in
BCA | Pile | Reinforcement Length | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | ReinforcementLength | Label | m | N.A | Fully reinforced, Unreinforced, 12, 18, 24, 30, 36
BCA | Pile | Reinforcement Steel Grade | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Pile | Stirrups | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | Stirrups | Label | N.A | N.A | 1H16-250
BCA | Pile | Structural Compression Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | StructuralCompressionCapacity | Integer | kN | N.A | 6525
BCA | Pile | Structural Tension Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | StructuralTensionCapacity | Integer | kN | N.A | 3825
BCA | Pile | ToeLevel_SHD | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | ToeLevel_SHD | Real | m | N.A | -63.35
BCA | Pile | Width | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Width | Length | mm | N.A | 600
BCA | Project Information | End Bearing R4 Design Factor | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | EndBearingR4DesignFactor | Real | N.A | N.A
BCA | Project Information | No Of Non Destructive Test Pile | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfNonDestructiveTestPile | Integer | N.A | N.A | 8
BCA | Project Information | No of ULT Test | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfULTTest | Integer | N.A | N.A | 2
BCA | Project Information | No of Working Load Test - Maintained Load Test | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfWorkingLoadTest_MaintainedLoadTest | Integer | N.A | N.A | 3
BCA | Project Information | No of Working Load Test - Rapid Load Test | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfWorkingLoadTest_RapidLoadTest | Integer | N.A | N.A | 3
BCA | Project Information | Pile Model Factor | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | PileModelFactor | Real | N.A | N.A | 1.35 / 1.55
BCA | Project Information | Shaft R4 Design Factor | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | ShaftR4DesignFactor | Real | N.A | N.A
PUB | Type Bedding for Pipe | BeddingType | Generic Models | Object | N.A | Object | External Works | IfcPipeSegment | *FOUNDATION | SGPset_PipeSegment | BeddingType | Label | N.A | N.A | Type 1, Type 2, Type 3
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SPRINKLER | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *WETRISER | N.A | N.A | N.A | N.A | N.A | N.A
BCA | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | CHILLEDWATER | N.A | N.A | N.A | N.A | N.A | N.A | Only Column J (IFC Sub Types)
BCA | System | Pre-insulated | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | CHILLEDWATER | SGPset_PipeSegment | PreInsulated | Label | N.A | N.A | N.A | New
BCA | System | Construction Method | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | CHILLEDWATER | SGPset_PipeSegment | ConstructionMethod | Label | N.A | N.A | N.A | New
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | FIREPROTECTION | N.A | N.A | N.A | N.A | N.A | N.A | Only Column J (IFC Sub Types)
NEA | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | RAINWATER | N.A | N.A | N.A | N.A | N.A | N.A | Only Column J (IFC Sub Types)
BCA | Project Information | Project Nature | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_ProjectDesignParameter | ProjectNature | Label | N.A | N.A | XXX | Removed
BCA | Project Information | Max No of Building Storey | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_ProjectDesignParameter | MaxNoOfBuildingStorey | Label | N.A | N.A | 36 | Removed
BCA | Project Information | Project Reference | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_ProjectInformation | ProjectReference | Label | N.A | N.A | A1234-12345-1234 | Removed
BCA | Project Information | Project Title | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_ProjectInformation | ProjectTitle | Label | N.A | N.A | Proposed XXX, long para | Removed
BCA | Project Information | QP Name | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_ProjectInformation | QPName | Label | N.A | N.A | XXX | Removed
BCA | Project Information | AC Name | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_ProjectInformation | ACName | Label | N.A | N.A | XXX | Removed
BCA | Project Information | QP Geo Name | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_ProjectInformation | QPGeoName | Label | N.A | N.A | XXX | Removed
BCA | Project Information | AC Geo Name | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_ProjectInformation | ACGeoName | Label | N.A | N.A | XXX | Removed
PUB | Pump | Capacity | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | Capacity | VolumetricFlowRate | L/s or m3/s | N.A | N.A | Only Column N (Property Unit)
PUB | Pump | Duty | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | Duty | Boolean | N.A | N.A | TRUE/FALSE
PUB | Pump | Standby Pump | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | Standby | Boolean | N.A | N.A | TRUE/FALSE
PUB | Pump | Pump Head | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | PumpHead | Label | m | N.A | 1m, 2m | Multiple Columns C, L, M, N, P (Identified Parameters, Property Name, Property Type, Property Unit, Sample Value for Reference)
BCA | Guardrail | Safety Barrier | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_Railing | SafetyBarrier | Boolean | N.A | N.A | TRUE/FALSE
BCA | Guardrail | Type of Barrier | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_Railing | TypeOfBarrier | Label | N.A | N.A | N.A
BCA | Guardrail | Is Laminated | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_Railing | IsLaminated | Boolean | N.A | N.A | TRUE/FALSE | Multiple Columns C, L, M, P (Identified Parameters, Property Name, Property Type, Sample Value for Reference)
BCA | Railing | Height | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_RailingDimension | Height | Length | mm | N.A | N.A
LTA | Ramp | Accessway | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Accessway | Boolean | N.A | N.A | TRUE/FALSE
NEA | Road | Accessway | Ramps | Ramp | Item | Object | ARC | IfcRamp | *DRIVEWAY | SGPset_Ramp | Accessway | Boolean | N.A | N.A | TRUE/FALSE
BCA | Ramp | Barrier Free Accessibility | Ramps | Ramp | Item | Object | ARC | IfcRamp | Need not specify | SGPset_Ramp | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Ramp | Barrier Free Accessibility | Ramps | Ramp | Item | Object | ARC | IfcRamp | *FLAREDKERBRAMP | SGPset_Ramp | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Ramp | Barrier Free Accessibility | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Egress | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Egress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Ingress | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Ingress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Transition Ramp | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_Ramp | TransitionRamp | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Vehicular | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_Ramp | Vehicular | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Vehicular | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Vehicular | Boolean | N.A | N.A | TRUE/FALSE
BCA | Ramp | Gradient | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_RampDimension | Gradient | Label | N.A | N.A | N.A
LTA | Ramp | Gradient | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_RampDimension | Gradient | Label | N.A | N.A | N.A
BCA | Ramp | Kerb Height | Ramps | Ramp | Item | Object | ARC | IfcRamp | Need not specify | SGPset_RampDimension | KerbHeight | Length | mm | N.A | N.A
BCA | Ramp | Width | Ramps | Ramp | Item | Object | ARC | IfcRamp | Need not specify | SGPset_RampDimension | Width | Label | N.A | N.A | N.A
LTA | Ramp | Width | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_RampDimension | Width | Label | N.A | N.A | N.A
LTA | Ramp | Width | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_RampDimension | Width | Label | N.A | N.A | N.A
PUB | Bath | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | BATH | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE | Multiple Columns C, K, L, M, P (Identified Parameters, Property Set, Property Name, Property Type)
PUB | Bidet | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | BIDET | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE | Multiple Columns C, K, L, M, P (Identified Parameters, Property Set, Property Name, Property Type)
PUB | Shower | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | SHOWER | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE | Multiple Columns C, K, L, M, P (Identified Parameters, Property Set, Property Name, Property Type)
PUB | Sink | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | SINK | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE | Multiple Columns C, K, L, M, P (Identified Parameters, Property Set, Property Name, Property Type)
PUB | Sink | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | SINK | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Urinal | Ambulant Disabled | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | AmbulantDisabled | Boolean | N.A | N.A | TRUE/FALSE
BCA | Urinal | Children Friendly | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE
BCA | Urinal | Children Friendly | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE | Removed
BCA | Urinal | Mounting | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | Mounting | Label | N.A | N.A | N.A
BCA | Urinal | Waterless | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | Waterless | Boolean | N.A | N.A | TRUE/FALSE
NEA | Wash Basin | Children Friendly | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | WASHHANDBASIN | SGPset_SanitaryTerminal | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE
NEA | Wash Basin | Mounting | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | WASHHANDBASIN | SGPset_SanitaryTerminal | Mounting | Label | N.A | N.A | N.A
NEA | Sensor | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcSensor | LEVELSENSOR | N.A | N.A | N.A | N.A | N.A | N.A | Removed
SCDF | Sensor | Smoke Detector Type | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcSensor | *FLAMEDETECTOR | SGPset_Sensor | SmokeDetectorType | Label | N.A | N.A | Point Type/ Optical | Removed
SCDF | Sensor | Engineered Smoke Control System | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcSensor | HEATSENSOR | SGPset_Sensor | EngineeredSmokeControlSystem | Boolean | N.A | N.A | TRUE/FALSE | Removed
SCDF | Sensor | Engineered Smoke Control System | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcSensor | SMOKESENSOR | SGPset_Sensor | EngineeredSmokeControlSystem | Boolean | N.A | N.A | TRUE/FALSE | Removed
BCA | Shading Device | Shading Device | Generic Models | Object | N.A | Object | ARC | IfcShadingDevice | *LOUVREDPANEL | SGPset_ShadingDevice | ShadingDevice | Label | N.A | N.A | N.A
URA | Chalet | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | ProjectDevelopmentType | Label | N.A | N.A | Holiday Resort | Removed
URA | Childcare Centre | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | ProjectDevelopmentType | Label | N.A | N.A | Children’S Home | Removed
URA | Commercial | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | ProjectDevelopmentType | Label | N.A | N.A | Commercial 2 | Removed
URA | Commercial | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | ProjectDevelopmentType | Label | N.A | N.A | Security office | Removed
URA | Community Centre | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | ProjectDevelopmentType | Label | N.A | N.A | Community Centre | Removed
URA | Independent Workers' Dormitory | Number of Workers | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | NumberOfWorkers | Integer | N.A | N.A | N.A
URA | Serviced Apartment | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | ProjectDevelopmentType | Label | N.A | N.A | Serviced Apartment | Removed
URA | Site | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | ProjectDevelopmentType | Label | N.A | N.A | Factory | Removed
URA | Site | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | ProjectDevelopmentType | Label | N.A | N.A | N.A
BCA | Slab | Mark | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabDimension | Mark | Label | N.A | N.A | S1
BCA | Wall | Mark | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallDimension | Mark | Label | N.A | N.A | W1
BCA | Wall | Material | Walls | Wall | Panel | Wall | ARC | IfcWall | Need not specify | SGPset_Material | Material | Label | N.A | Name | Reinforced Concrete | Only Column M (Property Type)
BCA | Slab | Material Grade | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete | Multiple Columns O, P (IFC4 Material Set, Sample Value for Reference)
BCA | Wall | Material Grade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete | Multiple Columns O, P (IFC4 Material Set, Sample Value for Reference)
URA | RC ledges (cantilevered) | N.A | Floors | Slab | Slab | Slab | ARC | IfcSlab | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Construction Method | Walls | Wall | Panel | Wall | ARC | IfcWall | *REFUSECHUTE | SGPset_Wall | ConstructionMethod | Label | N.A | N.A | N.A | Multiple Columns C, K, L, M (Identified Parameters, Property Set, Property Name, Property Type)
URA | Wall | N.A | Walls | Wall | Panel | Wall | ARC | IfcWall | PARAPET | N.A | N.A | N.A | N.A | N.A | N.A
URA | Wall | N.A | Walls | Wall | Panel | Wall | ARC | IfcWall | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Slab | ReferTo2DDetail | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Wall | ReferTo2DDetail | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Slab | Reinforcement Steel Grade | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Wall | Reinforcement Steel Grade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Slab | Shelter Usage | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ShelterUsage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Barrier Free Accessibility | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Accessible Route | Barrier Free Accessibility | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSIBLEROUTE | SGPset_Space | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Space | Elderly Friendly | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | ElderlyFriendly | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Space | Fire Emergency Ventilation Mode | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FireEmergencyVentilationMode | Label | N.A | N.A | Natural Ventilation, Mechanical Ventilation, Pressurisation, Cross-ventilation, Cross-ventilation with Intermediate Ventilation Opening, Vapour Extraction System (for spray painting room) | Only Column P (Sample Value for Reference)
SCDF | Space | Fire Exit | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FireExit | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Hearing Enhancement | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | HearingEnhancement | Boolean | N.A | N.A | TRUE/FALSE
BCA | Household Shelter | Height | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Height | Length | mm | N.A | N.A
BCA | Storey Shelter | Height | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Height | Length | mm | N.A | N.A
PUB | RC Tank | Height | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Height | Length | mm | N.A | N.A
BCA | Space | Height | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Height | Length | mm | N.A | N.A
BCA | Space | Larger Accessible | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | LargerAccessible | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Road | Loading Capacity | Areas | Zone | N.A | Space | ARC | IfcSpace | *FIREENGINEACCESSROAD | SGPset_Space | LoadingCapacity | Real | tonnes | N.A | 30 tonnes
SCDF | Road | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *FIREENGINEACCESSWAY | SGPset_Space | LoadingCapacity | Real | Tonnes | N.A | 24 tonnes
NEA | Road | Material | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSWAY | SGPset_Material | Material | Label | N.A | Name | N.A | New
NEA | Road | Material | Areas | Zone | N.A | Space | ARC | IfcSpace | *VEHICULARSERVICEROAD | SGPset_Material | Material | Label | N.A | Name | N.A | New
LTA | Space | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *EGRESS | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Space | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *INGRESS | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Road | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSWAY | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Road | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSROAD | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Space | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *EGRESS | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Space | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *INGRESS | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Road | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *VEHICULARSERVICEROAD | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Road | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *FIREENGINEACCESSROAD | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Space | Normal Ventilation Mode | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceThermalRequirements | NormalVentilationMode | Label | N.A | N.A | NaturalVentilation, AirConditioning MechanicalVentilation, MechanicalVentilation | Removed
URA | Space | Occupancy Type | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | OccupancyType | Label | N.A | N.A | Refer to list of Occupancy Types in Modelling IFC-SG (Space Usage) chapter of the CORENET X Code of Practice | Only Column P (Sample Value for Reference)
SCDF | Space | Occupancy Load | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | OccupancyLoad | Real | N.A | N.A | N.A | Multiple Columns C, K, L, M (Identified Parameters, Property Set, Property Name, Property Type)
SCDF | Space | Purpose Group | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | PurposeGroup | Label | N.A | N.A | I, II, III
BCA | Space | Retrofit | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | Retrofit | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Refer to list of Space Names in Modelling IFC-SG (Space Usage) chapter of the CORENET X Code of Practice | Only Column P (Sample Value for Reference)
BCA | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Lactation Room | Removed
NEA | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Car Washing Bay | Removed
NEA | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Common Area | Removed
NEA | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Kitchen | Removed
URA | AREA_CONNECTIVITY | ACN_ActivityGeneratingUseType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_ActivityGeneratingUseType | Label | N.A | N.A | N.A
URA | AREA_CONNECTIVITY | ACN_CloseTime | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_CloseTime | Label | N.A | N.A | N.A
URA | AREA_CONNECTIVITY | ACN_ConnectivityType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_ConnectivityType | Label | N.A | N.A | N.A
URA | AREA_CONNECTIVITY | ACN_IsOpen24HoursToPublic | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_IsOpen24HoursToPublic | Boolean | N.A | N.A | TRUE/FALSE | Only Column P (Sample Value for Reference)
URA | AREA_CONNECTIVITY | ACN_IsPavingSpecified | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_IsPavingSpecified | Boolean | N.A | N.A | TRUE/FALSE | Only Column P (Sample Value for Reference)
URA | AREA_CONNECTIVITY | ACN_OpenTime | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_OpenTime | Label | N.A | N.A | N.A
URA | AREA_CONNECTIVITY | ACN_PavingSpecification | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_PavingSpecification | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_AreaID | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_AreaID | Label | N.A | N.A | N.A | Removed
URA | AREA_GFA | AGF_BonusGFAType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_BonusGFAType | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_DetailedUse | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_DetailedUse | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_DevelopmentUse | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_DevelopmentUse | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_FacilityType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_FacilityType | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_Name | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_Name | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_Note | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_Note | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_PublicToiletID | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_PublicToiletID | Label | N.A | N.A | N.A | Removed
URA | AREA_GFA | AGF_RecyclablesChuteID | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_RecyclablesChuteID | Label | N.A | N.A | N.A | Removed
URA | AREA_GFA | AGF_RefuseChuteID | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_RefuseChuteID | Label | N.A | N.A | N.A | Removed
URA | AREA_GFA | AGF_UnitNumber | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_UnitNumber | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_UseQuantum | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_UseQuantum | Label | N.A | N.A | N.A
URA | AREA_LANDSCAPE | ALS_GreeneryFeatures | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_LANDSCAPE | SGPset_SpaceArea_Landscape | ALS_GreeneryFeatures | Label | N.A | N.A | N.A
URA | AREA_LANDSCAPE | ALS_LandscapeType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_LANDSCAPE | SGPset_SpaceArea_Landscape | ALS_LandscapeType | Label | N.A | N.A | N.A
URA | AREA_STRATA | AST_AreaType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_AreaType | Label | N.A | N.A | N.A
URA | AREA_STRATA | AST_Associated to | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_AssociatedTo | Label | N.A | N.A | N.A
URA | AREA_STRATA | AST_Extg_StrataLotNumber | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_Extg_StrataLotNumber | Label | N.A | N.A | N.A
URA | AREA_STRATA | AST_LegalArea | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_LegalArea | Integer | N.A | N.A | N.A
URA | AREA_STRATA | AST_Prop_StrataLotNumber | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_Prop_StrataLotNumber | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_AreaType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_AreaType | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_BonusGFAType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_BonusGFAType | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_DetailedUse | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_DetailedUse | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_DevelopmentUse | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_DevelopmentUse | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_Name | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_Name | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_UseQuantum | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_UseQuantum | Label | N.A | N.A | N.A
NEA | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Linkway | Removed
NEA | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Refuse Chute Chamber | Removed
NEA | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Refuse Room | Removed
NEA | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Sump Pit | Removed
PUB | RC Tank | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | RC Tank
SCDF | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | N.A | SGPset_Space | SpaceName | N.A | N.A | N.A | Dry Riser | Removed
SCDF | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Exit Staircase | Removed
SCDF | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Fire Command Center | Removed
SCDF | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Fire Lift Lobby | Removed
SCDF | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Special Purpose Room | Removed
SCDF | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | N.A | SGPset_Space | SpaceName | N.A | N.A | N.A | Wet Riser | Removed
BCA | Refuse Chute / Recyclables Chute | Space Name | Areas | Zone | N.A | Space | ARC | IfcSpace | *REFUSECHUTE | SGPset_Space | SpaceName | Label | N.A | N.A | Refuse Chute Chamber | New
SCDF | Space | Sprinkler Protection Automatic | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SprinklerProtectionAutomatic | Boolean | N.A | N.A | TRUE/FALSE | Removed
SCDF | Space | 24hr Manned Station | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | TwentyFourHourMannedStation | Boolean | N.A | N.A | TRUE/FALSE
URA | Space | Unit Number | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | UnitNumber | Label | N.A | N.A | N.A
BCA | Space | Ventilation Mode | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | VentilationMode | Label | N.A | N.A | Natural Ventilation, Air Conditioning, Mechanical Ventilation | Multiple Columns C, L, P (Identified Parameters, Property Name, Sample Value for Reference)
BCA | Staircase | Construction Method | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Staircase | Construction Method | Stairs | Stair | Component | Stair | ARC | IfcStair | Need not specify | SGPset_Stair | ConstructionMethod | Label | N.A | N.A | Prefabricated, Precast, Cast in-situ, Install on-site | Removed
BCA | Staircase | Mark | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | Mark | Label | N.A | N.A | ST1, ST-A1
BCA | Staircase | ReferTo2DDetail | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Staircase | Reinforcement Steel Grade | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Staircase | Section Fabrication Method | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | SectionFabricationMethod | Label | N.A | N.A | Hot rolled, Cold formed
BCA | Staircase | Member Section | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairDimension | MemberSection | Label | N.A | N.A | RHS600x30x4, CHS500x3.0, 254x254x63 kg/m
BCA | Staircase | Thickness | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairDimension | Thickness | Length | mm | N.A | 150
BCA | Staircase | Width | Stairs | Stair | Component | Stair | ARC | IfcStair | Need not specify | SGPset_StairDimension | Width | Length | mm | N.A | 2200
SCDF | Staircase | Width | Stairs | Stair | Component | Stair | ARC | IfcStair | Need not specify | SGPset_StairDimension | Width | Length | mm | N.A | N.A
BCA | Staircase | Bottom Distribution | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | BottomDistribution | Label | N.A | N.A | H25-150+H16-300
BCA | Staircase | Bottom Main | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | BottomMain | Label | N.A | N.A | H25-150+H16-300
BCA | Staircase | Top Distribution | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | TopDistribution | Label | N.A | N.A | H25-150+H16-300
BCA | Staircase | Top Main | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | TopMain | Label | N.A | N.A | H32-150+H20-300
BCA | Staircase | Connection Details Bottom | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionDetailsBottom | Label | N.A | N.A | Detail 1
BCA | Staircase | Connection Details Top | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionDetailsTop | Label | N.A | N.A | Detail 1
BCA | Staircase | Connection Type Bottom | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionTypeBottom | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Staircase | Connection Type Top | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionTypeTop | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Column | Connection Details Bottom | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionDetailsBottom | Label | N.A | N.A | Detail 1
BCA | Column | Connection Details Top | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionDetailsTop | Label | N.A | N.A | Detail 1
BCA | Column | Connection Type Bottom | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionTypeBottom | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Column | Connection Type Top | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionTypeTop | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Beam | Left Connection Detail | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | LeftConnectionDetail | Label | N.A | N.A | Detail 1 | Only Column P (Sample Value for Reference)
BCA | Beam | Left Connection Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | LeftConnectionType | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Beam | Right Connection Detail | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | RightConnectionDetail | Label | N.A | N.A | Detail 1 | Only Column P (Sample Value for Reference)
BCA | Beam | Right Connection Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | RightConnectionType | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Beam | Splice Connection | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | SpliceConnection | Label | N.A | N.A | Detail 3 | Only Column P (Sample Value for Reference)
BCA | Column | Splice Detail | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | SpliceDetail | Label | N.A | N.A | Detail 3
PUB | Tank | Height | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *POTABLEWATER | SGPset_TankDimension | Height | Length | mm | N.A | N.A
PUB | Tank | Thickness | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *POTABLEWATER | SGPset_TankDimension | Thickness | Length | mm | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *RAINWATERHARVESTINGTANK | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *RECHARGEWELL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Tank | Nominal Capacity | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *REFUSEHANDLINGEQUIPMENT | Pset_TankTypeCommon | NominalCapacity | Volume | L | N.A | N.A
NEA | Tank | Compaction Ratio | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *REFUSEHANDLINGEQUIPMENT | SGPset_Tank | CompactionRatio | Label | N.A | N.A | N.A
NEA | Tank | Equipment Type | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *REFUSEHANDLINGEQUIPMENT | SGPset_Tank | EquipmentType | Label | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *SECTIONAL | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *SPRINKLERTANK | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | Nominal Capacity | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | Pset_TankTypeCommon | NominalCapacity | Volume | L | N.A | N.A
PUB | Tank | Is Potable | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_Tank | IsPotable | Boolean | N.A | N.A | TRUE/FALSE
PUB | Tank | Height | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Height | Length | mm | N.A | N.A
BCA | Lift | Barrier Free Accessibility | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElement | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Lift | Barrier Free Accessibility | Mechanical Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *PLATFORMLIFT | SGPset_TransportElement | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Lift | Fire Fighting Lift | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElement | FireFightingLift | Boolean | N.A | N.A | TRUE/FALSE
BCA | Lift | Length | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | Length | Length | mm | N.A | N.A
BCA | Lift | Width | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | Width | Length | mm | N.A | N.A
SCDF | Lift | Clear Width | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | ClearWidth | Length | mm | N.A | N.A
SCDF | Lift | Clear Depth | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | ClearDepth | Length | mm | N.A | N.A
SCDF | Lift | Clear Height | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | ClearHeight | Length | mm | N.A | N.A
SCDF | Control Element | Alarm Panel | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | GASDETECTIONPANEL | SGPset_UnitaryControlElement | AlarmPanel | Boolean | N.A | N.A | TRUE/FALSE | Removed
SCDF | Control Element | Engineered Smoke Control System | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | CONTROLPANEL | SGPset_UnitaryControlElement | EngineeredSmokeControlSystem | Boolean | N.A | N.A | TRUE/FALSE | Removed
SCDF | Control Element | Fire Alarm Panel | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | ALARMPANEL | SGPset_UnitaryControlElement | FireAlarmPanel | Boolean | N.A | N.A | TRUE/FALSE | Removed
SCDF | Control Element | Purpose | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | ALARMPANEL | SGPset_UnitaryControlElement | Purpose | Label | N.A | N.A | Main Panel, Sub Panel
NEA | Control Panel | Flushing | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | CONTROLPANEL | SGPset_UnitaryControlElement | PWCS_Flushing | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Control Element | Smoke Control Panel | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | ALARMPANEL | SGPset_UnitaryControlElement | SmokeControlPanel | Boolean | N.A | N.A | TRUE/FALSE | Removed
SCDF | Control Element | Smoke Purging | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | CONTROLPANEL | SGPset_UnitaryControlElement | SmokePurging | Boolean | N.A | N.A | TRUE/FALSE | Removed
BCA | Wall | Shelter Usage | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ShelterUsage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Slab | Slab Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | SlabType | Label | N.A | N.A | One way, Two way, Cantilever, Flat slab, Flat slab with drop panel, Transfer slab
BCA | Slab | Stirrups | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | Stirrups | Label | N.A | N.A | 1H10-150-300
BCA | Wall | Stirrups | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | Stirrups | Label | N.A | N.A | H10-150-300
BCA | Slab | Stirrups Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion | Only Column P (Sample Value for Reference)
BCA | Wall | Stirrups Type | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion | Only Column P (Sample Value for Reference)
BCA | Slab | Thickness | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabDimension | Thickness | Length | mm | N.A | 300
BCA | Wall | Thickness | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallDimension | Thickness | Length | mm | N.A | 300
BCA | Slab | Top Distribution nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | TopDistribution_nominal | Label | N.A | N.A | H25-150+H16-300
BCA | Slab | Top Main Nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | TopMain_nominal | Label | N.A | N.A | H32-150+H20-300
BCA | Wall | Vertical Rebar | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | VerticalRebar | Label | N.A | N.A | H32-150+H25-150
BCA | Slab | Welded Mesh | Floors | Slab | Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | WeldedMesh | Boolean | N.A | N.A | TRUE/FALSE
BCA | Accessible Route | Width | Floors | Slab | Slab | Slab | ARC | IfcSlab | *ACCESSIBLEROUTE | SGPset_SlabDimension | Width | Length | mm | N.A | N.A | New
SCDF | Window | Fire Access Opening | Windows | Window | N.A | Window | ARC | IfcWindow | WINDOW | SGPset_Window | FireAccessOpening | Boolean | N.A | N.A | TRUE/FALSE
BCA | Window | Inner Diameter | Windows | Window | N.A | Window | ARC | IfcWindow | *VENTILATIONSLEEVE | SGPset_WindowDimension | InnerDiameter | Length | mm | N.A | N.A
BCA | Window | Outer Diameter | Windows | Window | N.A | Window | ARC | IfcWindow | *VENTILATIONSLEEVE | SGPset_WindowDimension | OuterDiameter | Length | mm | N.A | N.A
BCA | Window | Structural Width | Windows | Window | N.A | Window | ARC | IfcWindow | WINDOW | SGPset_WindowDimension | StructuralWidth | Length | mm | N.A | N.A
BCA | Window | Structural Height | Windows | Window | N.A | Window | ARC | IfcWindow | WINDOW | SGPset_WindowDimension | StructuralHeight | Length | mm | N.A | N.A
BCA | Wall | Working Load DA1-1 | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallStructuralLoad | WorkingLoad_DA1-1 | Integer | kN | N.A | 1234
BCA | Wall | Working Load DA1-2 | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallStructuralLoad | WorkingLoad_DA1-2 | Integer | kN | N.A | 1234
BCA | Accessible Route | Barrier Free Accessibility | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ACCESSIBLEROUTE | SGPset_CivilElement | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Accessible Route | Width | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ACCESSIBLEROUTE | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A | New
BCA | Accessible Route | Barrier Free Accessibility | Ramps | Ramp | Item | Object | ARC | IfcRamp | *ACCESSIBLEROUTE | SGPset_Ramp | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Accessible Route | Width | Ramps | Ramp | Item | Object | ARC | IfcRamp | *ACCESSIBLEROUTE | SGPset_RampDimension | Width | Length | mm | N.A | N.A | New
SCDF | Space | Ventilation Type | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | VentilationType | Label | N.A | N.A | CrossVentilation
BCA | Household Shelter | Volume | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Volume | Label | N.A | N.A | N.A
BCA | Beam | Accreditation PAS (Precaster Accreditation Scheme) | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Beam | Beam Cage | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BeamCage | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Beam | Prefabrication Reinforcement Cage | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | PrefabricationReinforcementCage | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Beam | Mechanical Connection Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | MechanicalConnectionType | Label | N.A | N.A | Telescopic Beam Connector | New
SCDF | Ceiling | Fire Rating | Ceilings | Ceiling | N.A | Slab | ARC | IfcCovering | CEILING | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A | New
SCDF | Ceiling | Material | Ceilings | Ceiling | N.A | Slab | ARC | IfcCovering | CEILING | SGPset_Material | Material | Label | N.A | Name | N.A | New
BCA | Column | Accreditation PAS (Precaster Accreditation Scheme) | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Column | Column Cage | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | ColumnCage | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Column | Prefabricated Reinforcement Cage | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | PrefabricationReinforcementCage | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Column | Mechanical Connection Type | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | MechanicalConnectionType | Label | N.A | N.A | Column Shoes | New
BCA | Column | Arrangement Type | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_PrecastConcreteElementGeneral | ArrangementType | Label | N.A | N.A | Multi-Tier | New
PUB | Culvert | Material | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_Material | Material | Label | N.A | Name | N.A | New
PUB | Distribution Chamber | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Length | Length | mm | N.A | N.A
PUB | Distribution Chamber | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Width | Length | mm | N.A | N.A
PUB | Distribution Chamber | Material | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_Material | Material | Label | N.A | Name | N.A | New
PUB | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | TRENCH | N.A | N.A | N.A | N.A | N.A | N.A | New
NEA | Distribution Chamber | Watertight | Generic Models | Covering | N.A | Slab | ARC | IfcCovering | *PWCSINSPECTIONCHAMBERCOVER | SGPset_Covering | Watertight | Boolean | N.A | N.A | TRUE/FALSE | New
NEA | Distribution Chamber | Watertight | Generic Models | Covering | N.A | Slab | ARC | IfcCovering | *PWCSMANHOLECOVER | SGPset_Covering | Watertight | Boolean | N.A | N.A | TRUE/FALSE | New
NEA | Distribution Chamber | External Reference | Generic Models | Covering | N.A | Slab | ARC | IfcCovering | *PWCSMANHOLECOVER | SGPset_Covering | ExternalReference | Label | N.A | N.A | SS 30 Manhole Tops and Surface-box Tops | New
SCDF | Door | Fire Exit | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | Pset_DoorCommon | FireExit | Boolean | N.A | N.A | TRUE/FALSE | New
SCDF | Door | Hardware | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | Hardware | Boolean | N.A | N.A | TRUE/FALSE | New
NEA | Door | Main Entrance | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | MainEntrance | Boolean | N.A | N.A | TRUE/FALSE | New
SCDF | Door | One Way Locking Device | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | OneWayLockingDevice | Boolean | N.A | N.A | TRUE/FALSE | New
NEA | Door | PanelDepth | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | PanelDepth | Length | mm | N.A | N.A | New
NEA | Door | PanelWidth | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | PanelWidth | Length | mm | N.A | N.A | New
BCA | Door | PowerOperated | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | PowerOperated | Boolean | N.A | N.A | TRUE/FALSE | New
SCDF | Door | Material | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Material | Material | Label | N.A | Name | N.A | New
SCDF | Door | Fire Access Opening | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | FireAccessOpening | Boolean | N.A | N.A | TRUE/FALSE | New
SCDF | Door | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | *ROLLERSHUTTER | Pset_DoorCommon | FireRating | Label | hr | N.A | N.A | New
SCDF | Door | Operation Type | Doors | Door | N.A | Door | ARC | IfcDoor | *ROLLERSHUTTER | SGPset_Door | OperationType | Label | N.A | N.A | N.A | New
PUB | Wash Basin | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | WASHHANDBASIN | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
URA | Earthworks | Area | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *EXISTINGEARTHWORKS | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A | New
URA | Earthworks | Area | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PROPOSEDEARTHWORKS | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A | New
BCA | Electrical Fixture for Household / Storey Shelter | OutletType | Electrical Fixtures | Object | N.A | Object | MEP | IfcSwitchingDevice | POWEROUTLET | SGPset_SwitchingDevice | OutletType | Label | N.A | N.A | N.A | New
BCA | Family-Friendly Furniture | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *CHILDPROTECTIONSEAT | N.A | N.A | N.A | N.A | N.A | N.A | New
BCA | Family-Friendly Furniture | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *DIAPERCHANGINGTABLE | N.A | N.A | N.A | N.A | N.A | N.A | New
SCDF | Finishes | Material | Generic Models | Model Element | N.A | Object | ARC | IfcCovering | CLADDING | SGPset_Material | Material | Label | N.A | Name | N.A | New
SCDF | Finishes | Fire Rating | Generic Models | Model Element | N.A | Object | ARC | IfcCovering | *FIRECURTAIN | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A | New
SCDF | Finishes | Fire Rating | Floors | Slab | Slab | Slab | ARC | IfcCovering | FLOORING | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A | New
SCDF | Finishes | Material | Floors | Slab | Slab | Slab | ARC | IfcCovering | FLOORING | SGPset_Material | Material | Label | N.A | Name | N.A | New
NEA | Finishes | Material | Generic Models | Object | N.A | Object | ARC | IfcCovering | *PIPESLEEVE | SGPset_Material | Material | Label | N.A | Name | N.A | New
SCDF | Opening | Fire Access Opening | Void | Opening | N.A | Opening | ARC | IfcOpeningElement | Need not specify | SGPset_OpeningElement | FireAccessOpening | Boolean | N.A | N.A | TRUE/FALSE | New
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *HOMEFIREALARMDEVICE | N.A | N.A | N.A | N.A | N.A | N.A | New
SCDF | Foam Inlet | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | MEP | IfcFireSuppressionTerminal | *FOAMINLET | N.A | N.A | N.A | N.A | N.A | N.A | New
SCDF | Foam Outlet | N.A | Plumbing Fixtures | Pipe | N.A | Equipment | MEP | IfcFireSuppressionTerminal | *FOAMOUTLET | N.A | N.A | N.A | N.A | N.A | N.A | New
BCA | Footing | Working Load DA1-2 | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FoundationStructuralLoad | WorkingLoad_DA1-2 | Integer | kN | N.A | 4321 | New
NPARKS | Green Verge | Shrub Species | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | ShrubSpecies | Label | N.A | N.A | N.A | New
NPARKS | Green Verge | Approved Turf Species | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | ApprovedTurfSpecies | Label | N.A | N.A | N.A | New
BCA | Wall | Accreditation PAS (Precaster Accreditation Scheme) | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Slab | Accreditation PAS (Precaster Accreditation Scheme) | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Household Shelter | Construction Method | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystem | ConstructionMethod | Label | N.A | N.A | Precast | New
BCA | Household Shelter | Accreditation PAS (Precaster Accreditation Scheme) | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystem | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Household Shelter | Inner Dimensions | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystemDimension | InnerDimensions | Label | N.A | N.A | N.A | New
BCA | Household Shelter | Area | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystemDimension | Area | Area | m2 | N.A | N.A | New
BCA | Household Shelter | Height | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystemDimension | Height | Length | mm | N.A | N.A | New
BCA | Household Shelter | Wall Thickness | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystemDimension | WallThickness | Length | mm | N.A | N.A | New
BCA | Household Shelter | Slab Thickness | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystemDimension | SlabThickness | Length | mm | N.A | N.A | New
NPARKS | Landscape Plants | Reason For Removal | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | ReasonForRemoval | Label | N.A | N.A | N.A | New
NPARKS | Landscape Plants | Tree Number | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | TreeNumber | Label | N.A | N.A | N.A | New
NPARKS | Landscape Plants | Height | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElementDimension | Height | Label | N.A | N.A | N.A | New
NPARKS | Landscape Plants | Roadside | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | Roadside | Boolean | N.A | N.A | TRUE/FALSE | New
SCDF | Lift | Lift Type | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElement | LiftType | Label | N.A | N | N.A | New
LTA | Parking Lot | Bicycle Rack Type | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxy | BicycleRack_Type | Label | N.A | N.A | Single Tier P Rack, Single Tier U Bar, Double Tier | New
BCA | Pipes / Drains | Pre-insulated | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Pipes / Drains | Construction Method | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | ConstructionMethod | Label | N.A | N.A | N.A | New
NPARKS | Pipes / Drains | Perforated | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | Perforated | Boolean | N.A | N.A | TRUE/FALSE | New
NPARKS | Pipes / Drains | Diameter | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A | New
PUB | Pipes / Drains | Material | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_Material | Material | Label | N.A | Name | N.A | New
PUB | Pipes / Drains | Gradient | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | Gradient | Label | N.A | N.A | N.A | New
PUB | Pipes / Drains | Length | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A | New
PUB | Pipes / Drains | Thickness | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegmentDimension | Thickness | Length | mm | N.A | N.A | New
NEA | Pipes / Drains | Trade Effluent | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Pipes / Drains | Pre-insulated | Flex Pipes | Pipe | N.A | Flexible Pipe | MEP | IfcPipeSegment | FLEXIBLESEGMENT | SGPset_PipeSegment | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Pipes / Drains | Construction Method | Flex Pipes | Pipe | N.A | Flexible Pipe | MEP | IfcPipeSegment | FLEXIBLESEGMENT | SGPset_PipeSegment | ConstructionMethod | Label | N.A | N.A | N.A | New
BCA | Pipes / Drains | Pre-insulated | Ducts | Duct | N.A | Duct | MEP | IfcDuctSegment | Need not specify | SGPset_DuctSegment | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Pipes / Drains | Construction Method | Ducts | Duct | N.A | Duct | MEP | IfcDuctSegment | Need not specify | SGPset_DuctSegment | ConstructionMethod | Label | N.A | N.A | N.A | New
BCA | Pipes / Drains | Pre-insulated | Duct Fittings | Duct Fitting | N.A | Duct Accessory | MEP | IfcDuctFitting | Need not specify | SGPset_DuctFitting | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Pipes / Drains | Construction Method | Duct Fittings | Duct Fitting | N.A | Duct Accessory | MEP | IfcDuctFitting | Need not specify | SGPset_DuctFitting | ConstructionMethod | Label | N.A | N.A | N.A | New
NEA | Pipes / Drains | Trade Effluent | Ducts | Duct | N.A | Duct | MEP | IfcDuctSegment | Need not specify | SGPset_DuctSegment | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE | New
NEA | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | *SCUPPERDRAIN | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | SPOOL | N.A | N.A | N.A | N.A | N.A | N.A | New
NEA | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | *FLARESTACK | N.A | N.A | N.A | N.A | N.A | N.A | New
NEA | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | *RAINWATEROUTLET | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Pipes / Drains | Material | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | BEND | SGPset_Material | Material | Label | N.A | Name | N.A | New
NEA | Pipes / Drains | Nominal Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | BEND | SGPset_PipeFittingDimension | NominalDiameter | Length | mm | N.A | N.A | New
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *DRAINCHANNELBEND | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | ENTRY | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | EXIT | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *FLANGEADAPTOR | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *FLEXIBLECOUPLING | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Pipes / Drains | Material | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | JUNCTION | SGPset_Material | Material | Label | N.A | Name | N.A | New
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | OBSTRUCTION | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Pipes / Drains | Material | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *PIPESILENCER | SGPset_Material | Material | Label | N.A | Name | N.A | New
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *SHORTPIECE | N.A | N.A | N.A | N.A | N.A | N.A | New
PUB | Pipes / Drains | Inner Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFittingDimension | InnerDiameter | Length | mm | N.A | N.A | New
NEA | Pipes / Drains | Nominal Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFittingDimension | NominalDiameter | Length | mm | N.A | N.A | New
PUB | Pipes / Drains | Outer Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFittingDimension | OuterDiameter | Length | mm | N.A | N.A | New
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Arsenic | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Barium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Barium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Beryllium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Beryllium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Biochemical Oxygen Demand | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_BiochemicalOxygenDemand | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Boron | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Boron | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Cadmium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Calcium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Calcium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Chemical Oxygen Demand | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_ChemicalOxygenDemand | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Chloride | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Chromium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Chromium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Colour | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Colour | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Copper | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Cyanide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Cyanide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Detergent | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Detergent | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Grease And Oil | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_GreaseAndOil | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Iron | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Iron | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Lead | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Magnesium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Magnesium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Manganese | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Manganese | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Mercury | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Metals In Total | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_MetalsInTotal | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Nickel | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Nickel | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Nitrate | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Nitrate | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge PH Value | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_PHValue | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Phenolic Compound | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_PhenolicCompound | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Phosphate | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Phosphate | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Selenium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Selenium | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Silver | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Silver | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Sulphate | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Sulphate | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Sulphide | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Temperature Of Discharge | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_TemperatureOfDischarge | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Tin | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Tin | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Total Dissolved Solid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_TotalDissolvedSolid | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Total Suspended Solid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_TotalSuspendedSolid | Label | N.A | N.A | N.A | New
NEA | Pollution Control | Trade Effluent Discharge Zinc | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Zinc | Label | N.A | N.A | N.A | New
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *PREFABRICATEDBATHROOMUNIT | N.A | N.A | N.A | N.A | N.A | N.A | New
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *PREFABRICATEDANDPREFINISHEDWALL | N.A | N.A | N.A | N.A | N.A | N.A | New
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *PREFABRICATEDANDPREFINISHEDFLOOR | N.A | N.A | N.A | N.A | N.A | N.A | New
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *PREFABRICATEDANDPREFINISHEDCEILING | N.A | N.A | N.A | N.A | N.A | N.A | New
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *PRECASTEXTERNALWALLWITHCASTINWINDOWS | N.A | N.A | N.A | N.A | N.A | N.A | New
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | MEP | IfcBuildingSystem | *PREFABRICATEDPUMPSKID | N.A | N.A | N.A | N.A | N.A | N.A | New
BCA | Prefabricated Building Systems and MEP Components | Mechanical Connection Type | Model Groups | IFC Assignments | N.A | System | MEP | IfcBuildingSystem | *PREFABRICATEDMEPVERTICALMODULE | SGPset_BuildingSystem | MechanicalConnectionType | Label | N.A | N.A | N.A | New
BCA | Prefabricated Building Systems and MEP Components | Mechanical Connection Type | Model Groups | IFC Assignments | N.A | System | MEP | IfcBuildingSystem | *PREFABRICATEDMEPPLANTMODULE | SGPset_BuildingSystem | MechanicalConnectionType | Label | N.A | N.A | N.A | New
BCA | Prefabricated Building Systems and MEP Components | Mechanical Connection Type | Model Groups | IFC Assignments | N.A | System | MEP | IfcBuildingSystem | *PREFABRICATEDMEPHORIZONTALMODULE | SGPset_BuildingSystem | MechanicalConnectionType | Label | N.A | N.A | N.A | New
BCA | Prefabricated Building Systems and MEP Components | Is Common | Generic Models | Object | N.A | Object | MEP | IfcDiscreteAccessory | *PIPESUPPORT | SGPset_DiscreteAccessory | IsCommon | Boolean | N.A | N.A | TRUE/FALSE | New
PUB | System | N.A | Piping Systems | MEP System | N.A | System | External Works | IfcDistributionSystem | RAINWATER | N.A | N.A | N.A | N.A | N.A | N.A | Only Column J (IFC Sub Types)
NEA | System | Gradient | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | RAINWATER | SGPset_PipeSegmentDimension | Gradient | Label | N.A | N.A | N.A | Only Column J (IFC Sub Types)
LTA | Ramp | Material | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Material | Material | Label | N.A | N.A | TRUE/FALSE | New
BCA | Storey Shelter | Volume | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Volume | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | Litre | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | Litre | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A | New
` | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | Litre | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | Litre | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A | New
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A | New
NEA | Refuse Handling Equipment | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSEBIN | N.A | N.A | N.A | N.A | N.A | N.A | New
SCDF | Road | Designed Vehicle Mass | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_CivilElement | DesignedVehicleMass | Real | N.A | N.A | 30 tonnes |  | New
LTA | Road | Material | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_Material | Material | Label | N.A | Name | N.A |  | New
LTA | Road | Road Category | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPSet_CivilElement | RoadCategory | Label | N.A | Name | N.A |  | New
PUB | RC Tank | Volume | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Volume | Label | N.A | N.A | N.A
BCA | Accessible Route | Width | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSIBLEROUTE | SGPset_SpaceDimension | Width | Length | mm | N.A | N.A | New
LTA | Road | N.A | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSPOINT | N.A | N.A | N.A | N.A | N.A | N.A | New
LTA | Road | Height | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A | New
LTA | Road | Material | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_Material | Material | Label | N.A | N.A | N.A | New
NParks | Roof | Construction Method | Roofs | Roof | N.A | Roof | ARC | IfcRoof | Need not specify | SGPset_Roof | ConstructionMethod | Label | N.A | N.A | N.A | New
NParks | Roof | Material | Roofs | Roof | N.A | Roof | ARC | IfcRoof | Need not specify | SGPset_Material | Material | Label | N.A | Name | N.A | New
NParks | Roof | Construction Method | Roofs | Slab | Slab | Slab | ARC | IfcSlab | ROOF | SGPset_Slab | ConstructionMethod | Label | N.A | N.A | N.A | New
NParks | Roof | Material | Roofs | Slab | Slab | Slab | ARC | IfcSlab | ROOF | SGPset_Material | Material | Label | N.A | Name | N.A | New
NParks | Roof | Construction Method | Roofs | Roof | N.A | Roof | ARC | IfcCovering | ROOFING | SGPset_Covering | ConstructionMethod | Label | N.A | N.A | N.A | New
NParks | Roof | Material | Roofs | Roof | N.A | Roof | ARC | IfcCovering | ROOFING | SGPset_Material | Material | Label | N.A | Name | N.A | New
PUB | Urinal | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE | New
PUB | Water Closet | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE | New
URA | Site Boundary | N.A | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *SITEBOUNDARY | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A | New
BCA | Slab | Slab Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Slab | Slab Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | MechanicalConnectionType | Label | N.A | N.A | N.A | New
BCA | Slab | Slab Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | Type Designator | Label | N.A | N.A | N.A | New
BCA | Slab | Slab Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | LatticeGirderReinforcement | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Space | Ambulant Disabled | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | AmbulantDisabled | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Space | Children Friendly | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE | New
PUB | Space | C Value | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | CValue | Label | N.A | N.A | 0.45 - 1 | New
SCDF | Space | Emergency Voice Communication System | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | EmergencyVoiceCommunicationSystem | Label | N.A | N.A | 1-way EVC System, 2-way EVC System, Public Address System | New
SCDF | Space | Fire Detection And Suppression System | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FireDetectionAndSuppressionSystem | Label | N.A | N.A | Automatic Fire Alarm System, Automatic Sprinkler System, Water Mist System, Video Image Fire Detector System, Kitchen Hood Fire Extinguishing System, Clean Agent Fire Extinguishing System, Automatic Foam Sprinkler System, Foam Extinguisher System | New
NParks | Space | Fully Covered With Tree Shrubs | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FullyCoveredWithTreesShrubs | Boolean | N.A | N.A | TRUE/FALSE | New
NEA | Space | Refuse Output | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | RefuseOutput | Real | N.A | N.A | 120, 200 | New
SCDF | Space | Smoke Control System | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SmokeControlSystem | Label | N.A | N.A | Smoke Vent, Smoke Purging System, Ductless Jet Fan System, Engineered Smoke Control System | New
NEA | Space | Sound Power Level | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SoundPowerLevel | Label | N.A | N.A | N.A | New
NEA | Space | Sound Pressure Level | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SoundPressureLevel | Label | N.A | N.A | N.A | New
BCA | Space | Step Ramp Access | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | StepRampAccess | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Staircase | Accreditation PAS (Precaster Accreditation Scheme) | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Staircase | Mechanical Connection Type | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | MechanicalConnectionType | Label | N.A | N.A | N.A | New
BCA | Staircase | Number of Treads | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | NumberOfTreads | Integer | N.A | N.A | N.A | New
PUB | System | Length | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DOMESTICCOLDWATER | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A | New
PUB | System | Material | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DOMESTICCOLDWATER | SGPset_Material | Material | Label | N.A | Name | N.A | New
PUB | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DOMESTICCOLDWATER | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A | New
PUB | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DRAINAGE | N.A | N.A | N.A | N.A | N.A | N.A | New
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *FOAMFIREEXTINGUISHING | N.A | N.A | N.A | N.A | N.A | N.A | New
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *FOAMSPRINKLER | N.A | N.A | N.A | N.A | N.A | N.A | New
NEA | System | Trade Effluent | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | SEWAGE | SGPset_PipeSegment | TradeEffluent | N.A | N.A | N.A | N.A | New
PUB | Tank | Length | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Length | Length | mm | N.A | N.A
PUB | Tank | Width | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Width | Length | mm | N.A | N.A
PUB | Tank | Diameter | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Diameter | Length | mm | N.A | N.A | New
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | VESSEL | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Space | Is Potable | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | IsPotable | Boolean | N.A | N.A | TRUE/FALSE | New
PUB | Space | NominalCapacity | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | NominalCapacity | Real | N.A | N.A | N.A | New
PUB | Space | NominalCapacity | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | Thickness | Length | N.A | N.A | N.A | New
URA | Wall | N.A | Walls | Wall | Panel | Wall | ARC | IfcWall | RETAININGWALL | N.A | N.A | N.A | N.A | N.A | N.A | New
BCA | Wall | Load Bearing | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Wall | Mechanical Connection Type | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | MechanicalConnectionType | Label | N.A | N.A | N.A | New
BCA | Wall | Prefabricated Reinforcement Cage | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | PrefabricationReinforcementCage | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Wall | Is Party Wall | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | IsPartyWall | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Wall | Is External | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | IsExternal | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Wall | Beam Façade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | BeamFacade | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Wall | Double Bay Façade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | Double Bay Façade | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Wall | Prefinished Façade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | Prefinished Façade | Boolean | N.A | N.A | TRUE/FALSE | New
BCA | Wall | Arrangement Type | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ArrangementType | Label | N.A | N.A | N.A | New
NEA | Waste Terminal | Trade Effluent | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | *WASTESUMP | SGPset_WasteTerminal | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE | New
URA | Window | Material | Windows | Window | N.A | Window | ARC | IfcWindow | Need not specify | SGPset_Material | Material | Label | N.A | Name | N.A | New
SCDF | Window | Safety Barrier Height | Windows | Window | N.A | Window | ARC | IfcWindow | Need not specify | SGPset_Window | SafetyBarrierHeight | Real | N.A | N.A | N.A | New

## CX Pilot Mapping (Faired Copy)
Agency | Identified Component | Identified parameters | Revit Representation | Archicad Representation | Tekla Structures Representation | Bentley OpenBuildings Representation | Discipline | IFC4 Entities | IFC Sub Types (* = USERDEFINED) | Property Set | Property Name | Property Type | Property Unit | IFC4 Material Set | Sample Value for Reference
BCA | Accessible Route | Barrier Free Accessibility | Floors | Slab | Slab | Slab | ARC | IfcSlab | *ACCESSIBLEROUTE | SGPset_Slab | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Slab | Bottom Distribution Nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | BottomDistribution_nominal | Label | N.A | N.A | H25-150+H16-300
BCA | Slab | Bottom Main Nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | BottomMain_nominal | Label | N.A | N.A | H25-150+H16-300
BCA | Slab | Construction Method | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Electrical Fixture for Household / Storey Shelter | OutletSocketType | Electrical Fixtures | Object | N.A | Object | MEP | IfcSwitchingDevice | POWEROUTLET | SGPset_SwitchingDevice | OutletSocketType | Label | N.A | N.A | N.A
LTA | Road | N.A | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Space | Precaster Accreditation Scheme Accreditation | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Household Shelter | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
BCA | Parking Lot | Barrier Free Accessibility | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
BCA | Space | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
BCA | Storey Shelter | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
BCA | Space | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *DRYRISER | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *HOSEREEL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Sprinkler (Non-Fire; for NEA) | N.A | Sprinklers | Terminal | N.A | Sprinkler | MEP | IfcSanitaryTerminal | *SPRINKLER | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Gutter | N.A | Plumbing Fixtures | Pipe | N.A | Drains&Basins | MEP | IfcPipeSegment | GUTTER | N.A | N.A | N.A | N.A | N.A | N.A
NEA | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *PWCSINSPECTIONCHAMBER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | RC Tank | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
PUB | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcBuildingSystem | *DRAINAGE | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Waste Terminal | N.A | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | FLOORTRAP | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Grating | N.A | Generic Models | Covering | N.A | Object | ARC | IfcDiscreteAccessory | *GRATING | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pump | N.A | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
PUB | System | Material | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
PUB | Water Closet | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | *WATERCLOSET | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Water Closet | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | *WATERCLOSET | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Water Closet | Ambulant Disabled | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | AmbulantDisabled | Boolean | N.A | N.A | TRUE/FALSE
BCA | Water Closet | Barrier Free Accessibility | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
NEA | Water Closet | Children Friendly | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE
PUB | Tank | Trade Effluent | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *BALANCINGTANK | SGPset_Tank | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *FIREALARMPANEL | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Breeching Inlet | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | ARC | IfcFireSuppressionTerminal | BREECHINGINLET | N.A | N.A | N.A | N.A | N.A | N.A
PUB | System | Length | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A
SCDF | Security Lighting | N.A | Lighting Fixtures | Object | N.A | Object | MEP | IfcLightFixture | SECURITYLIGHTING | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Space | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
NEA | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *RAINWATER | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
SCDF | Hose Reel | N.A | Mechanical Equipment | Pipe Flow Terminal | N.A | Fixture | ARC | IfcFireSuppressionTerminal | HOSEREEL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *LANDINGVALVE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Pump | N.A | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
PUB | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | N.A | N.A | N.A | N.A | N.A | N.A
PUB | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
PUB | System | Gradient | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | SGPset_PipeSegmentDimension | Gradient | Label | N.A | N.A | N.A
PUB | System | Length | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A
SCDF | Hose Reel | N.A | Mechanical Equipment | Pipe | N.A | Pipe | ARC | IfcFireSuppressionTerminal | *STANDBYFIREHOSE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | ARC | IfcAlarm | *MANUALALARMCALLPOINT | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *VISUALALARM | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | Nominal Capacity | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | Pset_TankTypeCommon | NominalCapacity | Volume | L | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SMOKECONTROL | N.A | N.A | N.A | N.A | N.A | N.A
URA | Window | Operation Type | Windows | Window | N.A | Window | ARC | IfcWindow | *BAYWINDOW | SGPset_Window | OperationType | Label | N.A | N.A | N.A
URA | Building Element | N.A | N.A | N.A | N.A | N.A | ARC | IfcElement | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Building Storey | N.A | Levels | Storey | N.A | Floor | ARC | IfcBuildingStorey | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Control Panel | N.A | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | CONTROLPANEL | N.A | N.A | N.A | N.A | N.A | N.A
URA | Gondola | N.A | Massing | Morph | N.A | Forms | ARC | IfcBuildingElementProxy | *GONDOLA | N.A | N.A | N.A | N.A | N.A | N.A
URA | Mechanical Equipment - Chiller | N.A | Mechanical Equipment | Object | N.A | Mechanical Equipment | MEP | IfcChiller | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Pump | N.A | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Mechanical Equipment - Unitary Equipment | N.A | Mechanical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryEquipment | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Site Boundary | N.A | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *CADASTRALLOT | N.A | N.A | N.A | N.A | N.A | N.A
URA | Planter Box | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *PLANTERBOX | N.A | N.A | N.A | N.A | N.A | N.A
URA | Roof | N.A | Roofs | Roof | N.A | Roof | ARC | IfcRoof | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Site Boundary | N.A | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *CADASTRALLOT | N.A | N.A | N.A | N.A | N.A | N.A
NPARKS | Site Boundary | Approved Soil Mixture | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *CADASTRALLOT | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
NEA | Water Closet | Pan Mounting | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | PanMounting | Label | N.A | N.A | N.A
BCA | Family-Friendly Furniture | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *CHANGINGBED | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Water Closet | Toilet Pan Type | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | ToiletPanType | Label | N.A | N.A | N.A
NParks | Culvert | N.A | Generic Models | Object | Slab, Panel | Drains&Basins | ARC | IfcCivilElement | *ENTRANCECULVERT | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | N.A | Doors | Door | N.A | Door | ARC | IfcDoor | *ACCESSHATCH | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Blast Door | Opening Height | Doors | Door | N.A | Door | ARC | IfcDoor | *BLASTDOOR | SGPset_DoorDimension | OpeningHeight | Length | mm | N.A | N.A
BCA | Blast Door | Opening Width | Doors | Door | N.A | Door | ARC | IfcDoor | *BLASTDOOR | SGPset_DoorDimension | OpeningWidth | Length | mm | N.A | N.A
BCA | Blast Door | Operation Type | Doors | Door | N.A | Door | ARC | IfcDoor | *BLASTDOOR | SGPset_Door | OperationType | Label | N.A | N.A | N.A
BCA | Lift | N.A | Mechanical Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | ESCALATOR | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *SOUNDER | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *SPRINKLERCONTROL | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | DOUBLECHECK | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | MIXING | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *REFLUXVALVE | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *AIRADMITTANCE | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *DRAINOFFCOCK | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | CHECK | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | ISOLATING | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Lift | N.A | Mechanical Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *GOODSLIFT | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Lift | N.A | Mechanical Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *BINLIFTER | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Balustrade | N.A | Railings | Railing | Component | Railing | STR | IfcRailing | BALUSTRADE | N.A | N.A | N.A | N.A | N.A | N.A
URA | Bollard | N.A | Railings | Railing | Component | Railing | STR | IfcRailing | *BOLLARD | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Footpath | Material | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *FOOTPATH | SGPset_Material | Material | Label | N.A | Name | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SMOKEPURGING | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | Is Potable | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_Tank | IsPotable | Boolean | N.A | N.A | TRUE/FALSE
PUB | Tank | Height | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_TankDimension | Height | Length | mm | N.A | N.A
PUB | Tank | Length | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_TankDimension | Length | Length | mm | N.A | N.A
PUB | Tank | Width | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_TankDimension | Width | Length | mm | N.A | N.A
BCA | Window | N.A | Windows | Window | N.A | Window | ARC | IfcWindow | SKYLIGHT | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Parking Lot | Bicycle Lot Count | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxy | BicycleLotCount | Integer | N.A | N.A | Limited to 1 or 2 only
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *PWCSMANHOLE | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *SAMPLINGSUMP | SGPset_DistributionChamberElement | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Control Element | N.A | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | *AUTOMATICRESCUEDEVICE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Control Element | N.A | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | *LIFTSUPERVISORYPANEL | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Soffit | Fire Rating | Roofs | Roof | N.A | Roof | ARC | IfcCovering | *SOFFIT | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | N.A | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEACCESSPANEL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | Pset_DoorCommon | FireRating | Label | hr | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Air Tight | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | SGPset_Door | AirTight | Boolean | N.A | N.A | TRUE/FALSE
PUB | Water Meter | Purpose | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | Purpose | Label | N.A | N.A | PRIVATE
PUB | Water Meter | Unit Number | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | UnitNumber | Label | N.A | N.A | N.A
PUB | Water Meter | Unit Number Tag | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | UnitNumberTag | Boolean | N.A | N.A | TRUE/FALSE
PUB | Water Meter | Water Supply Source | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | WaterSupplySource | Label | N.A | N.A | N.A
BCA | Chair | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | CHAIR | N.A | N.A | N.A | N.A | N.A | N.A
URA | Site | Total Area | Topography | Mesh | N.A | Mesh | ARC | IfcSite | Need not specify | Pset_SiteCommon | TotalArea | Area | m2 | N.A | N.A
SCDF | Staircase | Fire Exit | Stairs | Stair | Component | Stair | ARC | IfcStair | Need not specify | Pset_StairCommon | FireExit | Boolean | N.A | N.A | TRUE/FALSE
BCA | Staircase | Riser Count | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | NumberOfRisers | Integer | N.A | N.A | N.A
BCA | Staircase | Riser Height | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | RiserHeight | Length | mm | N.A | N.A
BCA | Staircase | Tread Width | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | TreadLength | Length | mm | N.A | N.A
SCDF | Staircase | Riser Height | Stairs | Stair | Item | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | RiserHeight | Length | mm | N.A | N.A
SCDF | Staircase | Tread Length | Stairs | Stair | Item | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | TreadLength | Length | mm | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *EJECTORTANK | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *IRRIGATIONTANK | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | Nominal Capacity | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *POTABLEWATER | Pset_TankTypeCommon | NominalCapacity | Volume | L | N.A | N.A
PUB | Tank | Diameter | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *POTABLEWATER | SGPset_TankDimension | Diameter | Length | mm | N.A | N.A
BCA | Wall | Construction Method | Walls | Wall | Panel | Wall | ARC | IfcWall | Need not specify | SGPset_Wall | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Beam | Beam Span Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | BeamSpanType | Label | N.A | N.A | Single, End, Interior, Cantilever
BCA | Beam | Construction Method | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Beam | Construction Method | Structural Framing | Beam | Beam | Beam | ARC | IfcBeam | Need not specify | SGPset_Beam | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Beam | ReferTo2DDetail | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Beam | Reinforcement Steel Grade | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Beam | Section Fabrication Method | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | SectionFabricationMethod | Label | N.A | N.A | Hot rolled, Cold formed
BCA | Beam | Depth | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | Depth | Length | mm | N.A | 600
BCA | Beam | Mark | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | Mark | Label | N.A | N.A | HB1, VB1, B1
BCA | Beam | Member Section | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | MemberSection | Label | N.A | N.A | RHS600x30x4, CHS500x3.0, 254x254x63 kg/m
BCA | Beam | Width | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | Width | Length | mm | N.A | 300
BCA | Beam | Bottom Left | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BottomLeft | Label | N.A | N.A | 3H25
BCA | Beam | Bottom Middle | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BottomMiddle | Label | N.A | N.A | 3H32+3H25+3H20
BCA | Beam | Bottom Right | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BottomRight | Label | N.A | N.A | 3H25
BCA | Beam | Stirrups Left | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsLeft | Label | N.A | N.A | 4H13-300
BCA | Beam | Side Bar | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | SideBar | Label | N.A | N.A | H13-250
BCA | Beam | Stirrups Middle | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsMiddle | Label | N.A | N.A | 4H13-300
BCA | Beam | Stirrups Right | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsRight | Label | N.A | N.A | 4H13-300
BCA | Beam | Top Left | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | TopLeft | Label | N.A | N.A | 3H32+3H25
BCA | Beam | Top Middle | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | TopMiddle | Label | N.A | N.A | 3H25
BCA | Beam | Top Right | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | TopRight | Label | N.A | N.A | 3H32+3H25
BCA | Beam | Stirrups Type Left | Structural Framing | Beam | Concrete Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsTypeLeft | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Beam | Stirrups Type Middle | Structural Framing | Beam | Concrete Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsTypeMiddle | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Beam | Stirrups Type Right | Structural Framing | Beam | Concrete Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsTypeRight | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
URA | Building | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | N.A
URA | Independent Workers' Dormitory | Number of Workers | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | NumberOfWorkers | Integer | N.A | N.A | N.A
BCA | Accessible Route | Barrier Free Accessibility | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSIBLEROUTE | SGPset_BuildingElementProxy | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Car Parking Served By Car Lift | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | CarParking_ServedByCarLift | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | EV Lot | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | EVLot | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Bicycle Lot Count | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLERACK | SGPset_BuildingElementProxy | BicycleLotCount | Integer | N.A | N.A | N.A
LTA | Parking Lot | Bicycle Parking Rack Type | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLERACK | SGPset_BuildingElementProxy | BicycleParkingRack_Type | Label | N.A | N.A | Single Tier, Double Tier
BCA | Parking Lot | Family Parking Lot | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | Family Lot | Boolean | N.A | N.A | TRUE/FALSE
BCA | Parking Lot | Length | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
SCDF | Fire Extinguisher | Fire Extinguisher Rating | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *PORTABLEFIREEXTINGUISHER | SGPset_BuildingElementProxy | FireExtinguisherRating | Label | N.A | N.A | 70B
SCDF | Road | Loading Capacity | Areas | Zone | N.A | Space | ARC | IfcBuildingElementProxy | *FIREENGINEACCESSWAY | SGPset_BuildingElementProxy | LoadingCapacity | Real | Tonnes | N.A | 24 tonnes
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
SCDF | Signage | Mounting Height | Specialty Equipment | Object | N.A | Object | ARC | IfcBuildingElementProxy | *SIGNAGE_EXIT | SGPset_BuildingElementProxy | MountingHeight | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Lot Number | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | LotNumber | Label | N.A | N.A | N.A
LTA | Parking Lot | N.A | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Parking Lot | N.A | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BUSLOT | N.A | N.A | N.A | N.A | N.A | N.A
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
BCA | Borehole | Depth | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | Depth | Length | mm | N.A | 14560
LTA | Parking Lot | Parking Use | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | ParkingUse | Label | N.A | N.A | Electric Vehicle, Oil Tanker, Buggy, Vacuum Truck, Mobile Tanker
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Vehicle Type | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | VehicleType | Label | N.A | N.A | Rigid-framed vehicle
BCA | Borehole | Mark | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | Mark | Label | N.A | N.A | BH1
BCA | Borehole | SHD Level SPT MoreThan 100N | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | SHDLevel_SPT_MoreThan_100N | Real | m | N.A | -27.5
BCA | Borehole | SHD Level SPT MoreThan 60N | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | SHDLevel_SPT_MoreThan_60N | Real | m | N.A | -15
BCA | Borehole | Termination Level | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | TerminationLevel | Real | m | N.A | -50.45
BCA | Borehole | Top Level | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | TopLevel | Real | m | N.A | 1.8
BCA | Accessible Route | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSIBLEROUTE | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
BCA | Parking Lot | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
URA | Attic Level | Attic Level | Levels | Storey | N.A | Floor | ARC | IfcBuildingStorey | Need not specify | SGPset_BuildingStorey | AtticLevel | Boolean | N.A | N.A | TRUE/FALSE
BCA | Refuse Chute / Recyclables Chute | Construction Method | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *REFUSECHUTE | SGPset_BuildingSystem | ConstructionMethod | Label | N.A | N.A | Prefabricated, Precast, Cast in-situ, Install on-site
BCA | Refuse Chute / Recyclables Chute | Outer Dimensions | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *REFUSECHUTE | SGPset_BuildingSystemDimension | OuterDimensions | Length | mm | N.A | N.A
BCA | Refuse Chute / Recyclables Chute | Inner Dimensions | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *REFUSECHUTE | SGPset_BuildingSystemDimension | InnerDimensions | Length | mm | N.A | N.A
BCA | Refuse Chute / Recyclables Chute | Chamfer Radius | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *REFUSECHUTE | SGPset_BuildingSystemDimension | ChamferRadius | Length | mm | N.A | N.A
PUB | Gutter | Construction Method | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElement | ConstructionMethod | Label | N.A | N.A | N.A
LTA | Road | Ingress | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_CivilElement | Egress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Culvert | Footpath | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | CULVERT | SGPset_CivilElement | Footpath | Boolean | N.A | N.A | TRUE/FALSE
LTA | Road | Egress | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_CivilElement | Ingress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Road | Kerb Type | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_CivilElement | KerbType | Label | N.A | N.A | N.A
LTA | Culvert | Load Bearing | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | CULVERT | SGPset_CivilElement | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Public | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElement | Public | Boolean | N.A | N.A | TRUE/FALSE
PUB | Gutter | Public | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElement | Public | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Diameter | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Culvert | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Gutter | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Culvert | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Gutter | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Culvert | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Gutter | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
LTA | Road | Thickness | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Culvert | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
PUB | Gutter | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
BCA | Column | Construction Method | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Column | Construction Method | Columns | Column | Concrete Column | Column | ARC | IfcColumn | Need not specify | SGPset_Column | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Column | ReferTo2DDetail | Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Column | Reinforcement Steel Grade | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Column | Section Fabrication Method | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | SectionFabricationMethod | Label | N.A | N.A | Hot rolled, Cold formed
BCA | Column | Breadth | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Breadth | Length | mm | N.A | 300
BCA | Column | Diameter | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Diameter | Length | mm | N.A | 600
BCA | Column | End Storey | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | EndStorey | Label | N.A | N.A | 2nd Storey, Roof Storey
BCA | Column | Mark | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Mark | Label | N.A | N.A | TC1, C1
BCA | Column | Member Section | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | MemberSection | Label | N.A | N.A | RHS600x30x4, CHS500x3.0, 254x254x63 kg/m
BCA | Column | Starting Storey | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | StartingStorey | Label | N.A | N.A | 1st Storey, Lower Roof Storey
BCA | Column | Width | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Width | Length | mm | N.A | 600
BCA | Column | Stirrups | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | Stirrups | Label | N.A | N.A | 4H13-300
BCA | Column | Stirrups Type | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Column | Main Rebar | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | MainRebar | Label | N.A | N.A | 6H32+6H25
BCA | Column | Working Load DA1-1 | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnStructuralLoad | WorkingLoad_DA1-1 | Integer | kN | N.A | 1234
BCA | Column | Working Load DA1-2 | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnStructuralLoad | WorkingLoad_DA1-2 | Integer | kN | N.A | 1234
SCDF | Damper | Fire Rating | Duct Accessories | Object | N.A | Object | MEP | IfcDamper | FIREDAMPER | SGPset_Damper | FireRating | Label | hr | N.A | 30min, 60min, 90min, 120min, 150min, 180min, 210min, 240min
SCDF | Damper | Fire Rating | Duct Accessories | Object | N.A | Object | MEP | IfcDamper | FIRESMOKEDAMPER | SGPset_Damper | FireRating | Label | hr | N.A | 30min, 60min, 90min, 120min, 150min, 180min, 210min, 240min
SCDF | Damper | Fire Rating | Duct Accessories | Object | N.A | Object | MEP | IfcDamper | SMOKEDAMPER | SGPset_Damper | FireRating | Label | hr | N.A | 30min, 60min, 90min, 120min, 150min, 180min, 210min, 240min
PUB | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *SCREENCHAMBER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Distribution Chamber | Depth | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Depth | Length | mm | N.A | N.A
PUB | Distribution Chamber | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Distribution Chamber | Height | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Height | Length | mm | N.A | N.A
PUB | Distribution Chamber | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Length | Length | mm | N.A | N.A
PUB | Distribution Chamber | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Width | Length | mm | N.A | N.A
PUB | Distribution Chamber | Material | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Distribution Chamber | Depth | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | Depth | Length | mm | N.A | N.A
PUB | Distribution Chamber | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Distribution Chamber | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | METERCHAMBER | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Distribution Chamber | Depth | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Depth | Length | mm | N.A | N.A
PUB | Distribution Chamber | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Diameter | Length | mm | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Self Closing | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | SGPset_Door | SelfClosing | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | Volume Controlled | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | SGPset_Door | VolumeControlled | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | N.A | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEACCESSPANEL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | Pset_DoorCommon | FireRating | Label | hr | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Air Tight | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | SGPset_Door | AirTight | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | Self Closing | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | SGPset_Door | SelfClosing | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | Volume Controlled | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | SGPset_Door | VolumeControlled | Boolean | N.A | N.A | TRUE/FALSE
LTA | Gate | N.A | Doors | Door | N.A | Door | ARC | IfcDoor | GATE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Door | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | Pset_DoorCommon | FireRating | Label | hr | N.A | N.A
SCDF | Door | Operation Type | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | OperationType | Label | N.A | N.A | N.A
SCDF | Door | Self Closing | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | SelfClosing | Boolean | N.A | N.A | TRUE/FALSE
BCA | Door | Vision Panel | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | VisionPanel | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | Clear Height | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | ClearHeight | Length | mm | N.A | N.A
SCDF | Door | Clear Width | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | ClearWidth | Length | mm | N.A | N.A
BCA | Door | Overall Width | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | OverallWidth | Length | mm | N.A | N.A
BCA | Door | StructuralHeight | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | StructuralHeight | Length | mm | N.A | N.A
BCA | Door | StructuralWidth | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | StructuralWidth | Length | mm | N.A | N.A
SCDF | Breeching Inlet | Hose Nominal Diameter | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | MEP | IfcFireSuppressionTerminal | BREECHINGINLET | SGPset_FireSuppressionTerminal | Hose_NominalDiameter | Label | N.A | N.A | N.A
SCDF | Hose Reel | Hose Nominal Diameter | Mechanical Equipment | Pipe Flow Terminal | N.A | Fixture | MEP | IfcFireSuppressionTerminal | HOSEREEL | SGPset_FireSuppressionTerminal | Hose_NominalDiameter | Label | mm | N.A | N.A
SCDF | Hose Reel | Hose Nominal Diameter | Mechanical Equipment | Pipe | N.A | Pipe | MEP | IfcFireSuppressionTerminal | *STANDBYFIREHOSE | SGPset_FireSuppressionTerminal | Hose_NominalDiameter | Label | mm | N.A | N.A
SCDF | Breeching Inlet | ID | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | MEP | IfcFireSuppressionTerminal | BREECHINGINLET | SGPset_FireSuppressionTerminal | ID | Label | N.A | N.A | N.A
SCDF | Fire Hydrant | ID | Plumbing Fixtures | Object | N.A | Fire Protection | MEP | IfcFireSuppressionTerminal | FIREHYDRANT | SGPset_FireSuppressionTerminal | ID | Label | N.A | N.A | N.A
SCDF | Fire Hydrant | Private | Plumbing Fixtures | Object | N.A | Fire Protection | MEP | IfcFireSuppressionTerminal | FIREHYDRANT | SGPset_FireSuppressionTerminal | Private | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Fire Hydrant | Public | Plumbing Fixtures | Object | N.A | Fire Protection | MEP | IfcFireSuppressionTerminal | FIREHYDRANT | SGPset_FireSuppressionTerminal | Public | Boolean | N.A | N.A | TRUE/FALSE
PUB | Water Meter | Capacity | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | SGPset_FlowMeter | Capacity | Volume | L/s | N.A | N.A
PUB | Water Meter | Diameter | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | SGPset_FlowMeterDimension | Diameter | Length | mm | N.A | N.A
PUB | Water Meter | Length | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | SGPset_FlowMeterDimension | Length | Length | mm | N.A | N.A
BCA | Footing | DA1-1 Bearing Capacity | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | DA1-1_BearingCapacity | Integer | kPa | N.A | 150
BCA | Footing | DA1-2 Bearing Capacity | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | DA1-2_BearingCapacity | Integer | kPa | N.A | 120
BCA | Footing | ReferTo2DDetail | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Footing | Reinforcement Steel Grade | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Footing | Soil Verification Test | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | SoilVerificationTest | Label | N.A | N.A | 2 nos plate load Test
BCA | Footing | Breadth | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Breadth | Length | mm | N.A | 6200
BCA | Footing | Depth | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Depth | Length | mm | N.A | 300
BCA | Footing | Mark | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Mark | Label | N.A | N.A | F2, PC1, PC2, PC4_1
BCA | Footing | Width | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Width | Length | mm | N.A | 300
BCA | Footing | Side Bar | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | SideBar | Label | N.A | N.A | H13-250
BCA | Footing | Stirrups | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | Stirrups | Label | N.A | N.A | H13-200-300
BCA | Footing | Stirrups Type | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Footing | Top Distribution | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | TopDistribution | Label | N.A | N.A | H16-150
BCA | Footing | Bottom Distribution | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | BottomDistribution | Label | N.A | N.A | H16-150
BCA | Footing | Bottom Main | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | BottomMain | Label | N.A | N.A | H25-150
BCA | Footing | Top Main | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | TopMain | Label | N.A | N.A | H25-150
BCA | Footing | Working Load DA1-1 | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FoundationStructuralLoad | WorkingLoad_DA1-1 | Integer | kN | N.A | 4321
BCA | Cubicle | Barrier Free Accessibility | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *CUBICLE | SGPset_Furniture | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Cubicle | Ambulant Disabled | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *CUBICLE | SGPset_Furniture | AmbulantDisabled | Boolean | N.A | N.A | TRUE/FALSE
NEA | Bench | Capacity | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *BENCH | SGPset_Furniture | Capacity | Label | N.A | N.A | N.A
NPARKS | Site Boundary | Area | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *CADASTRALLOT | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
NPARKS | Green Verge | Approved Soil Mixture | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Green Verge | Shrubs | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | Shrubs | Label | N.A | N.A | N.A
NPARKS | Green Verge | Area | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
NPARKS | Landscape Plants | Approved Soil Mixture | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_EXTERNALPLANTING | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Landscape Plants | Girth | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElementDimension | Girth | Length | mm | N.A | N.A
NPARKS | Landscape Plants | Girth | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElementDimension | Girth | Length | mm | N.A | N.A
NPARKS | Landscape Plants | Palm Type | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | PalmType | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Reason For Removal | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | ReasonForRemoval | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Single Stem | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | SingleStem | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Landscape Plants | Single Stem | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | SingleStem | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Landscape Plants | Species | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | Species | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Species | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_SHRUBS | SGPset_GeographicElement | Species | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Species | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | Species | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Status | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | Status | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Status | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_SHRUBS | SGPset_GeographicElement | Status | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Status | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | Status | Label | N.A | N.A | To be retained, To be felled/removed, To be transplanted, To be planted/proposed/new
NPARKS | Landscape Plants | Height | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElementDimension | Height | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Tree Number | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | TreeNumber | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Tree Size | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | TreeSize | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Tree Size | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | TreeSize | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Turf | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_SHRUBS | SGPset_GeographicElement | Turf | Boolean | N.A | N.A | TRUE/FALSE
URA | Neighbouring Lot | N.A | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *NEIGHBOURINGLOT | N.A | N.A | N.A | N.A | N.A | N.A
NPARKS | Planting Area | Approved Soil Mixture | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
URA | Soil | Approved Soil Mixture | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Carpark Provision | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | CarparkProvision | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Compensated | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | Compensated | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Status | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | Status | Label | N.A | N.A | N.A
NPARKS | Planting Area | Turf | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | Turf | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Turf Species | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | TurfSpecies | Label | N.A | N.A | N.A
NPARKS | Planting Area | Area | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
PUB | Interceptor | Comply to PUB Standard Drawing | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_Interceptor | ComplyToPUBStandardDrawing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Interceptor | Comply to PUB Standard Drawing | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_Interceptor | ComplyToPUBStandardDrawing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Interceptor | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Diameter | Length | N.A | N.A | N.A
PUB | Interceptor | Height | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Height | Length | N.A | N.A | N.A
PUB | Interceptor | Height | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | Height | Length | N.A | N.A | N.A
PUB | Interceptor | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Length | Length | N.A | N.A | N.A
PUB | Interceptor | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | Length | Length | N.A | N.A | N.A
PUB | Interceptor | Refer to Drawing Number | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_Interceptor | ReferToDrawingNumber | Label | N.A | N.A | N.A
PUB | Interceptor | Refer to Drawing Number | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_Interceptor | ReferToDrawingNumber | Label | N.A | N.A | N.A
PUB | Interceptor | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Width | Length | N.A | N.A | N.A
PUB | Interceptor | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | Width | Length | N.A | N.A | N.A
BCA | Beam | Material Grade | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Pile | Borehole Ref | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | BoreholeRef | Label | N.A | N.A | BH2, BH3, BH12-2
BCA | Column | Material Grade | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Wall | Construction Method | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
SCDF | Wall | Fire Rating | Walls | Wall | Panel | Wall | ARC | IfcWall | Need not specify | Pset_WallCommon | FireRating | Label | hr | N.A | N.A
BCA | Railing | Material | Railings | Railing | Component | Railing | STR | IfcRailing | GUARDRAIL | SGPset_Material | Material | Label | N.A | Name | N.A
BCA | Wall | Horizontal Rebar | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | HorizontalRebar | Label | N.A | N.A | H20-150
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SMOKEVENT | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Staircase | Material Grade | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Footing | Material Grade | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | FLOORTRAP | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | FLOORWASTE | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | GULLYSUMP | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | GULLYTRAP | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | WASTETRAP | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | *WASTESUMP | SGPset_Material | Material | Label | N.A | Name | N.A
BCA | Pile | Breadth | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Breadth | Length | mm | N.A | 300
BCA | Pile | Construction Method | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC, Spun
BCA | Pile | CutOffLevel_SHD | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | CutOffLevel_SHD | Real | m | N.A | -1.35
BCA | Pile | DA1-1 Compression Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-1_CompressionCapacity | Integer | kN | N.A | 5683
BCA | Pile | DA1-1 Compression Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-1_CompressionDesignLoad | Integer | kN | N.A | 5515
BCA | Pile | DA1-1 Tension Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-1_TensionCapacity | Integer | kN | N.A | 3655
BCA | Pile | DA1-1 Tension Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-1_TensionDesignLoad | Integer | kN | N.A | 3255
BCA | Pile | DA1-2 Compression Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-2_CompressionCapacity | Integer | kN | N.A | 4823
BCA | Pile | DA1-2 Compression Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-2_CompressionDesignLoad | Integer | kN | N.A | 4650
BCA | Pile | DA1-2 Tension Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-2_TensionCapacity | Integer | kN | N.A | 3025
BCA | Pile | DA1-2 Tension Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-2_TensionDesignLoad | Integer | kN | N.A | 2850
BCA | Pile | Diameter | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Diameter | Length | mm | N.A | 600
BCA | Pile | Length | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Length | Length | mm | N.A | 40000
BCA | Pile | Main Rebar | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | MainRebar | Label | N.A | N.A | 10H32+10H16
BCA | Pile | Mark | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Mark | Label | N.A | N.A | P156
BCA | Pile | Material Grade | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Pile | Member Section | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | MemberSection | Label | N.A | N.A | CHS500x3.0, 254x254x63 kg/m
BCA | Pile | Min Embedment Into Bearing Layer SPT More Than 100 N | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | MinEmbedmentIntoBearingLayer_SPT_MoreThan_100N | Real | m | N.A | 16.5
BCA | Pile | Min Embedment Into Bearing Layer SPT More Than 60 N | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | MinEmbedmentIntoBearingLayer_SPT_MoreThan_60N | Real | m | N.A | 23.2
BCA | Pile | Min Rock Socketing Length | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | MinRockSocketingLength | Real | m | N.A | 16.5
BCA | Pile | Negative Skin Friction | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | NegativeSkinFriction | Integer | kN | N.A | 135
BCA | Pile | Pile Type | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | PileType | Label | N.A | N.A | Driven, Bored, Jacked in
BCA | Pile | Reinforcement Length | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | ReinforcementLength | Label | m | N.A | Fully reinforced, Unreinforced, 12, 18, 24, 30, 36
BCA | Pile | Reinforcement Steel Grade | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Pile | Stirrups | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | Stirrups | Label | N.A | N.A | 1H16-250
BCA | Pile | Structural Compression Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | StructuralCompressionCapacity | Integer | kN | N.A | 6525
BCA | Pile | Structural Tension Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | StructuralTensionCapacity | Integer | kN | N.A | 3825
BCA | Pile | ToeLevel_SHD | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | ToeLevel_SHD | Real | m | N.A | -63.35
BCA | Pile | Width | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Width | Length | mm | N.A | 600
BCA | Project Information | End Bearing R4 Design Factor | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | EndBearingR4DesignFactor | Real | N.A | N.A
BCA | Project Information | No Of Non Destructive Test Pile | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfNonDestructiveTestPile | Integer | N.A | N.A | 8
BCA | Project Information | No of ULT Test | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfULTTest | Integer | N.A | N.A | 2
BCA | Project Information | No of Working Load Test - Maintained Load Test | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfWorkingLoadTest_MaintainedLoadTest | Integer | N.A | N.A | 3
BCA | Project Information | No of Working Load Test - Rapid Load Test | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfWorkingLoadTest_RapidLoadTest | Integer | N.A | N.A | 3
BCA | Project Information | Pile Model Factor | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | PileModelFactor | Real | N.A | N.A | 1.35 / 1.55
BCA | Project Information | Shaft R4 Design Factor | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | ShaftR4DesignFactor | Real | N.A | N.A
PUB | Type Bedding for Pipe | BeddingType | Generic Models | Object | N.A | Object | External Works | IfcPipeSegment | *FOUNDATION | SGPset_PipeSegment | BeddingType | Label | N.A | N.A | Type 1, Type 2, Type 3
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SPRINKLER | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *WETRISER | N.A | N.A | N.A | N.A | N.A | N.A
BCA | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | CHILLEDWATER | N.A | N.A | N.A | N.A | N.A | N.A
BCA | System | Pre-insulated | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | CHILLEDWATER | SGPset_PipeSegment | PreInsulated | Label | N.A | N.A | N.A
BCA | System | Construction Method | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | CHILLEDWATER | SGPset_PipeSegment | ConstructionMethod | Label | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | FIREPROTECTION | N.A | N.A | N.A | N.A | N.A | N.A
NEA | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | RAINWATER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pump | Capacity | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | Capacity | VolumetricFlowRate | L/s or m3/s | N.A | N.A
PUB | Pump | Duty | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | Duty | Boolean | N.A | N.A | TRUE/FALSE
PUB | Pump | Standby Pump | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | Standby | Boolean | N.A | N.A | TRUE/FALSE
PUB | Pump | Pump Head | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | PumpHead | Label | m | N.A | 1m, 2m
BCA | Guardrail | Safety Barrier | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_Railing | SafetyBarrier | Boolean | N.A | N.A | TRUE/FALSE
BCA | Guardrail | Type of Barrier | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_Railing | TypeOfBarrier | Label | N.A | N.A | N.A
BCA | Guardrail | Is Laminated | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_Railing | IsLaminated | Boolean | N.A | N.A | TRUE/FALSE
BCA | Railing | Height | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_RailingDimension | Height | Length | mm | N.A | N.A
LTA | Ramp | Accessway | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Accessway | Boolean | N.A | N.A | TRUE/FALSE
NEA | Road | Accessway | Ramps | Ramp | Item | Object | ARC | IfcRamp | *DRIVEWAY | SGPset_Ramp | Accessway | Boolean | N.A | N.A | TRUE/FALSE
BCA | Ramp | Barrier Free Accessibility | Ramps | Ramp | Item | Object | ARC | IfcRamp | Need not specify | SGPset_Ramp | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Ramp | Barrier Free Accessibility | Ramps | Ramp | Item | Object | ARC | IfcRamp | *FLAREDKERBRAMP | SGPset_Ramp | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Ramp | Barrier Free Accessibility | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Egress | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Egress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Ingress | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Ingress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Transition Ramp | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_Ramp | TransitionRamp | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Vehicular | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_Ramp | Vehicular | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Vehicular | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Vehicular | Boolean | N.A | N.A | TRUE/FALSE
BCA | Ramp | Gradient | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_RampDimension | Gradient | Label | N.A | N.A | N.A
LTA | Ramp | Gradient | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_RampDimension | Gradient | Label | N.A | N.A | N.A
BCA | Ramp | Kerb Height | Ramps | Ramp | Item | Object | ARC | IfcRamp | Need not specify | SGPset_RampDimension | KerbHeight | Length | mm | N.A | N.A
BCA | Ramp | Width | Ramps | Ramp | Item | Object | ARC | IfcRamp | Need not specify | SGPset_RampDimension | Width | Label | N.A | N.A | N.A
LTA | Ramp | Width | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_RampDimension | Width | Label | N.A | N.A | N.A
LTA | Ramp | Width | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_RampDimension | Width | Label | N.A | N.A | N.A
PUB | Bath | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | BATH | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
PUB | Bidet | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | BIDET | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
PUB | Shower | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | SHOWER | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
PUB | Sink | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | SINK | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
PUB | Sink | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | SINK | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Urinal | Ambulant Disabled | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | AmbulantDisabled | Boolean | N.A | N.A | TRUE/FALSE
BCA | Urinal | Children Friendly | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE
BCA | Urinal | Mounting | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | Mounting | Label | N.A | N.A | N.A
BCA | Urinal | Waterless | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | Waterless | Boolean | N.A | N.A | TRUE/FALSE
NEA | Wash Basin | Children Friendly | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | WASHHANDBASIN | SGPset_SanitaryTerminal | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE
NEA | Wash Basin | Mounting | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | WASHHANDBASIN | SGPset_SanitaryTerminal | Mounting | Label | N.A | N.A | N.A
NEA | Sensor | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcSensor | LEVELSENSOR | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Shading Device | Shading Device | Generic Models | Object | N.A | Object | ARC | IfcShadingDevice | *LOUVREDPANEL | SGPset_ShadingDevice | ShadingDevice | Label | N.A | N.A | N.A
URA | Independent Workers' Dormitory | Number of Workers | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | NumberOfWorkers | Integer | N.A | N.A | N.A
URA | Site | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | ProjectDevelopmentType | Label | N.A | N.A | N.A
BCA | Slab | Mark | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabDimension | Mark | Label | N.A | N.A | S1
BCA | Wall | Mark | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallDimension | Mark | Label | N.A | N.A | W1
BCA | Wall | Material | Walls | Wall | Panel | Wall | ARC | IfcWall | Need not specify | SGPset_Material | Material | Label | N.A | Name | Reinforced Concrete
BCA | Slab | Material Grade | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Wall | Material Grade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
URA | RC ledges (cantilevered) | N.A | Floors | Slab | Slab | Slab | ARC | IfcSlab | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Construction Method | Walls | Wall | Panel | Wall | ARC | IfcWall | *REFUSECHUTE | SGPset_Wall | ConstructionMethod | Label | N.A | N.A | N.A
URA | Wall | N.A | Walls | Wall | Panel | Wall | ARC | IfcWall | PARAPET | N.A | N.A | N.A | N.A | N.A | N.A
URA | Wall | N.A | Walls | Wall | Panel | Wall | ARC | IfcWall | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Slab | ReferTo2DDetail | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Wall | ReferTo2DDetail | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Slab | Reinforcement Steel Grade | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Wall | Reinforcement Steel Grade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Slab | Shelter Usage | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ShelterUsage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Barrier Free Accessibility | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Accessible Route | Barrier Free Accessibility | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSIBLEROUTE | SGPset_Space | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Elderly Friendly | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | ElderlyFriendly | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Space | Fire Emergency Ventilation Mode | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FireEmergencyVentilationMode | Label | N.A | N.A | Natural Ventilation, Mechanical Ventilation, Pressurisation, Cross-ventilation, Cross-ventilation with Intermediate Ventilation Opening, Vapour Extraction System (for spray painting room)
SCDF | Space | Fire Exit | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FireExit | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Hearing Enhancement | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | HearingEnhancement | Boolean | N.A | N.A | TRUE/FALSE
BCA | Household Shelter | Height | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Height | Length | mm | N.A | N.A
BCA | Storey Shelter | Height | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Height | Length | mm | N.A | N.A
PUB | RC Tank | Height | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Height | Length | mm | N.A | N.A
BCA | Space | Height | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Height | Length | mm | N.A | N.A
BCA | Space | Larger Accessible | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | LargerAccessible | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Road | Loading Capacity | Areas | Zone | N.A | Space | ARC | IfcSpace | *FIREENGINEACCESSROAD | SGPset_Space | LoadingCapacity | Real | tonnes | N.A | 30 tonnes
SCDF | Road | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *FIREENGINEACCESSWAY | SGPset_Space | LoadingCapacity | Real | Tonnes | N.A | 24 tonnes
NEA | Road | Material | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSWAY | SGPset_Material | Material | Label | N.A | Name | N.A
NEA | Road | Material | Areas | Zone | N.A | Space | ARC | IfcSpace | *VEHICULARSERVICEROAD | SGPset_Material | Material | Label | N.A | Name | N.A
LTA | Space | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *EGRESS | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Space | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *INGRESS | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Road | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSWAY | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Road | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSROAD | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Space | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *EGRESS | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Space | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *INGRESS | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Road | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *VEHICULARSERVICEROAD | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Road | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *FIREENGINEACCESSROAD | N.A | N.A | N.A | N.A | N.A | N.A
URA | Space | Occupancy Type | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | OccupancyType | Label | N.A | N.A | Refer to list of Occupancy Types in Modelling IFC-SG (Space Usage) chapter of the CORENET X Code of Practice
SCDF | Space | Occupancy Load | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | OccupancyLoad | Real | N.A | N.A | N.A
SCDF | Space | Purpose Group | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | PurposeGroup | Label | N.A | N.A | I, II, III
BCA | Space | Retrofit | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | Retrofit | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Refer to list of Space Names in Modelling IFC-SG (Space Usage) chapter of the CORENET X Code of Practice
URA | AREA_CONNECTIVITY | ACN_ActivityGeneratingUseType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_ActivityGeneratingUseType | Label | N.A | N.A | N.A
URA | AREA_CONNECTIVITY | ACN_CloseTime | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_CloseTime | Label | N.A | N.A | N.A
URA | AREA_CONNECTIVITY | ACN_ConnectivityType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_ConnectivityType | Label | N.A | N.A | N.A
URA | AREA_CONNECTIVITY | ACN_IsOpen24HoursToPublic | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_IsOpen24HoursToPublic | Boolean | N.A | N.A | TRUE/FALSE
URA | AREA_CONNECTIVITY | ACN_IsPavingSpecified | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_IsPavingSpecified | Boolean | N.A | N.A | TRUE/FALSE
URA | AREA_CONNECTIVITY | ACN_OpenTime | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_OpenTime | Label | N.A | N.A | N.A
URA | AREA_CONNECTIVITY | ACN_PavingSpecification | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_PavingSpecification | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_BonusGFAType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_BonusGFAType | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_DetailedUse | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_DetailedUse | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_DevelopmentUse | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_DevelopmentUse | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_FacilityType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_FacilityType | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_Name | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_Name | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_Note | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_Note | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_UnitNumber | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_UnitNumber | Label | N.A | N.A | N.A
URA | AREA_GFA | AGF_UseQuantum | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_UseQuantum | Label | N.A | N.A | N.A
URA | AREA_LANDSCAPE | ALS_GreeneryFeatures | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_LANDSCAPE | SGPset_SpaceArea_Landscape | ALS_GreeneryFeatures | Label | N.A | N.A | N.A
URA | AREA_LANDSCAPE | ALS_LandscapeType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_LANDSCAPE | SGPset_SpaceArea_Landscape | ALS_LandscapeType | Label | N.A | N.A | N.A
URA | AREA_STRATA | AST_AreaType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_AreaType | Label | N.A | N.A | N.A
URA | AREA_STRATA | AST_Associated to | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_AssociatedTo | Label | N.A | N.A | N.A
URA | AREA_STRATA | AST_Extg_StrataLotNumber | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_Extg_StrataLotNumber | Label | N.A | N.A | N.A
URA | AREA_STRATA | AST_LegalArea | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_LegalArea | Integer | N.A | N.A | N.A
URA | AREA_STRATA | AST_Prop_StrataLotNumber | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_Prop_StrataLotNumber | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_AreaType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_AreaType | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_BonusGFAType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_BonusGFAType | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_DetailedUse | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_DetailedUse | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_DevelopmentUse | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_DevelopmentUse | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_Name | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_Name | Label | N.A | N.A | N.A
URA | AREA_VERIFICATION | AVF_UseQuantum | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_VERIFICATION | SGPset_SpaceArea_Verification | AVF_UseQuantum | Label | N.A | N.A | N.A
PUB | RC Tank | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | RC Tank
BCA | Refuse Chute / Recyclables Chute | Space Name | Areas | Zone | N.A | Space | ARC | IfcSpace | *REFUSECHUTE | SGPset_Space | SpaceName | Label | N.A | N.A | Refuse Chute Chamber
SCDF | Space | 24hr Manned Station | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | TwentyFourHourMannedStation | Boolean | N.A | N.A | TRUE/FALSE
URA | Space | Unit Number | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | UnitNumber | Label | N.A | N.A | N.A
BCA | Space | Ventilation Mode | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | VentilationMode | Label | N.A | N.A | Natural Ventilation, Air Conditioning, Mechanical Ventilation
BCA | Staircase | Construction Method | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Staircase | Mark | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | Mark | Label | N.A | N.A | ST1, ST-A1
BCA | Staircase | ReferTo2DDetail | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Staircase | Reinforcement Steel Grade | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Staircase | Section Fabrication Method | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | SectionFabricationMethod | Label | N.A | N.A | Hot rolled, Cold formed
BCA | Staircase | Member Section | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairDimension | MemberSection | Label | N.A | N.A | RHS600x30x4, CHS500x3.0, 254x254x63 kg/m
BCA | Staircase | Thickness | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairDimension | Thickness | Length | mm | N.A | 150
BCA | Staircase | Width | Stairs | Stair | Component | Stair | ARC | IfcStair | Need not specify | SGPset_StairDimension | Width | Length | mm | N.A | 2200
SCDF | Staircase | Width | Stairs | Stair | Component | Stair | ARC | IfcStair | Need not specify | SGPset_StairDimension | Width | Length | mm | N.A | N.A
BCA | Staircase | Bottom Distribution | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | BottomDistribution | Label | N.A | N.A | H25-150+H16-300
BCA | Staircase | Bottom Main | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | BottomMain | Label | N.A | N.A | H25-150+H16-300
BCA | Staircase | Top Distribution | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | TopDistribution | Label | N.A | N.A | H25-150+H16-300
BCA | Staircase | Top Main | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | TopMain | Label | N.A | N.A | H32-150+H20-300
BCA | Staircase | Connection Details Bottom | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionDetailsBottom | Label | N.A | N.A | Detail 1
BCA | Staircase | Connection Details Top | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionDetailsTop | Label | N.A | N.A | Detail 1
BCA | Staircase | Connection Type Bottom | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionTypeBottom | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Staircase | Connection Type Top | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionTypeTop | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Column | Connection Details Bottom | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionDetailsBottom | Label | N.A | N.A | Detail 1
BCA | Column | Connection Details Top | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionDetailsTop | Label | N.A | N.A | Detail 1
BCA | Column | Connection Type Bottom | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionTypeBottom | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Column | Connection Type Top | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionTypeTop | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Beam | Left Connection Detail | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | LeftConnectionDetail | Label | N.A | N.A | Detail 1
BCA | Beam | Left Connection Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | LeftConnectionType | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Beam | Right Connection Detail | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | RightConnectionDetail | Label | N.A | N.A | Detail 1
BCA | Beam | Right Connection Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | RightConnectionType | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Beam | Splice Connection | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | SpliceConnection | Label | N.A | N.A | Detail 3
BCA | Column | Splice Detail | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | SpliceDetail | Label | N.A | N.A | Detail 3
PUB | Tank | Height | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *POTABLEWATER | SGPset_TankDimension | Height | Length | mm | N.A | N.A
PUB | Tank | Thickness | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *POTABLEWATER | SGPset_TankDimension | Thickness | Length | mm | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *RAINWATERHARVESTINGTANK | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *RECHARGEWELL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Tank | Nominal Capacity | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *REFUSEHANDLINGEQUIPMENT | Pset_TankTypeCommon | NominalCapacity | Volume | L | N.A | N.A
NEA | Tank | Compaction Ratio | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *REFUSEHANDLINGEQUIPMENT | SGPset_Tank | CompactionRatio | Label | N.A | N.A | N.A
NEA | Tank | Equipment Type | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *REFUSEHANDLINGEQUIPMENT | SGPset_Tank | EquipmentType | Label | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *SECTIONAL | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *SPRINKLERTANK | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | Nominal Capacity | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | Pset_TankTypeCommon | NominalCapacity | Volume | L | N.A | N.A
PUB | Tank | Is Potable | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_Tank | IsPotable | Boolean | N.A | N.A | TRUE/FALSE
PUB | Tank | Height | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Height | Length | mm | N.A | N.A
BCA | Lift | Barrier Free Accessibility | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElement | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Lift | Barrier Free Accessibility | Mechanical Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *PLATFORMLIFT | SGPset_TransportElement | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Lift | Fire Fighting Lift | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElement | FireFightingLift | Boolean | N.A | N.A | TRUE/FALSE
BCA | Lift | Length | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | Length | Length | mm | N.A | N.A
BCA | Lift | Width | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | Width | Length | mm | N.A | N.A
SCDF | Lift | Clear Width | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | ClearWidth | Length | mm | N.A | N.A
SCDF | Lift | Clear Depth | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | ClearDepth | Length | mm | N.A | N.A
SCDF | Lift | Clear Height | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | ClearHeight | Length | mm | N.A | N.A
SCDF | Control Element | Purpose | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | ALARMPANEL | SGPset_UnitaryControlElement | Purpose | Label | N.A | N.A | Main Panel, Sub Panel
NEA | Control Panel | Flushing | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | CONTROLPANEL | SGPset_UnitaryControlElement | PWCS_Flushing | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Shelter Usage | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ShelterUsage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Slab | Slab Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | SlabType | Label | N.A | N.A | One way, Two way, Cantilever, Flat slab, Flat slab with drop panel, Transfer slab
BCA | Slab | Stirrups | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | Stirrups | Label | N.A | N.A | 1H10-150-300
BCA | Wall | Stirrups | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | Stirrups | Label | N.A | N.A | H10-150-300
BCA | Slab | Stirrups Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Wall | Stirrups Type | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Slab | Thickness | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabDimension | Thickness | Length | mm | N.A | 300
BCA | Wall | Thickness | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallDimension | Thickness | Length | mm | N.A | 300
BCA | Slab | Top Distribution nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | TopDistribution_nominal | Label | N.A | N.A | H25-150+H16-300
BCA | Slab | Top Main Nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | TopMain_nominal | Label | N.A | N.A | H32-150+H20-300
BCA | Wall | Vertical Rebar | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | VerticalRebar | Label | N.A | N.A | H32-150+H25-150
BCA | Slab | Welded Mesh | Floors | Slab | Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | WeldedMesh | Boolean | N.A | N.A | TRUE/FALSE
BCA | Accessible Route | Width | Floors | Slab | Slab | Slab | ARC | IfcSlab | *ACCESSIBLEROUTE | SGPset_SlabDimension | Width | Length | mm | N.A | N.A
SCDF | Window | Fire Access Opening | Windows | Window | N.A | Window | ARC | IfcWindow | WINDOW | SGPset_Window | FireAccessOpening | Boolean | N.A | N.A | TRUE/FALSE
BCA | Window | Inner Diameter | Windows | Window | N.A | Window | ARC | IfcWindow | *VENTILATIONSLEEVE | SGPset_WindowDimension | InnerDiameter | Length | mm | N.A | N.A
BCA | Window | Outer Diameter | Windows | Window | N.A | Window | ARC | IfcWindow | *VENTILATIONSLEEVE | SGPset_WindowDimension | OuterDiameter | Length | mm | N.A | N.A
BCA | Window | Structural Width | Windows | Window | N.A | Window | ARC | IfcWindow | WINDOW | SGPset_WindowDimension | StructuralWidth | Length | mm | N.A | N.A
BCA | Window | Structural Height | Windows | Window | N.A | Window | ARC | IfcWindow | WINDOW | SGPset_WindowDimension | StructuralHeight | Length | mm | N.A | N.A
BCA | Wall | Working Load DA1-1 | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallStructuralLoad | WorkingLoad_DA1-1 | Integer | kN | N.A | 1234
BCA | Wall | Working Load DA1-2 | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallStructuralLoad | WorkingLoad_DA1-2 | Integer | kN | N.A | 1234
BCA | Accessible Route | Barrier Free Accessibility | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ACCESSIBLEROUTE | SGPset_CivilElement | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Accessible Route | Width | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ACCESSIBLEROUTE | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
BCA | Accessible Route | Barrier Free Accessibility | Ramps | Ramp | Item | Object | ARC | IfcRamp | *ACCESSIBLEROUTE | SGPset_Ramp | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Accessible Route | Width | Ramps | Ramp | Item | Object | ARC | IfcRamp | *ACCESSIBLEROUTE | SGPset_RampDimension | Width | Length | mm | N.A | N.A
SCDF | Space | Ventilation Type | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | VentilationType | Label | N.A | N.A | CrossVentilation
BCA | Household Shelter | Volume | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Volume | Label | N.A | N.A | N.A
BCA | Beam | Accreditation PAS (Precaster Accreditation Scheme) | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Beam | Beam Cage | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BeamCage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Beam | Prefabrication Reinforcement Cage | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | PrefabricationReinforcementCage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Beam | Mechanical Connection Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | MechanicalConnectionType | Label | N.A | N.A | Telescopic Beam Connector
SCDF | Ceiling | Fire Rating | Ceilings | Ceiling | N.A | Slab | ARC | IfcCovering | CEILING | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A
SCDF | Ceiling | Material | Ceilings | Ceiling | N.A | Slab | ARC | IfcCovering | CEILING | SGPset_Material | Material | Label | N.A | Name | N.A
BCA | Column | Accreditation PAS (Precaster Accreditation Scheme) | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Column | Column Cage | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | ColumnCage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Column | Prefabricated Reinforcement Cage | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | PrefabricationReinforcementCage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Column | Mechanical Connection Type | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | MechanicalConnectionType | Label | N.A | N.A | Column Shoes
BCA | Column | Arrangement Type | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_PrecastConcreteElementGeneral | ArrangementType | Label | N.A | N.A | Multi-Tier
PUB | Culvert | Material | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | CULVERT | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Distribution Chamber | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Length | Length | mm | N.A | N.A
PUB | Distribution Chamber | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Width | Length | mm | N.A | N.A
PUB | Distribution Chamber | Material | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | TRENCH | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Distribution Chamber | Watertight | Generic Models | Covering | N.A | Slab | ARC | IfcCovering | *PWCSINSPECTIONCHAMBERCOVER | SGPset_Covering | Watertight | Boolean | N.A | N.A | TRUE/FALSE
NEA | Distribution Chamber | Watertight | Generic Models | Covering | N.A | Slab | ARC | IfcCovering | *PWCSMANHOLECOVER | SGPset_Covering | Watertight | Boolean | N.A | N.A | TRUE/FALSE
NEA | Distribution Chamber | External Reference | Generic Models | Covering | N.A | Slab | ARC | IfcCovering | *PWCSMANHOLECOVER | SGPset_Covering | ExternalReference | Label | N.A | N.A | SS 30 Manhole Tops and Surface-box Tops
SCDF | Door | Fire Exit | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | Pset_DoorCommon | FireExit | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | Hardware | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | Hardware | Boolean | N.A | N.A | TRUE/FALSE
NEA | Door | Main Entrance | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | MainEntrance | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | One Way Locking Device | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | OneWayLockingDevice | Boolean | N.A | N.A | TRUE/FALSE
NEA | Door | PanelDepth | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | PanelDepth | Length | mm | N.A | N.A
NEA | Door | PanelWidth | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | PanelWidth | Length | mm | N.A | N.A
BCA | Door | PowerOperated | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | PowerOperated | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | Material | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Material | Material | Label | N.A | Name | N.A
SCDF | Door | Fire Access Opening | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | FireAccessOpening | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | *ROLLERSHUTTER | Pset_DoorCommon | FireRating | Label | hr | N.A | N.A
SCDF | Door | Operation Type | Doors | Door | N.A | Door | ARC | IfcDoor | *ROLLERSHUTTER | SGPset_Door | OperationType | Label | N.A | N.A | N.A
PUB | Wash Basin | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | WASHHANDBASIN | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
URA | Earthworks | Area | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *EXISTINGEARTHWORKS | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
URA | Earthworks | Area | Topography | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PROPOSEDEARTHWORKS | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
BCA | Electrical Fixture for Household / Storey Shelter | OutletType | Electrical Fixtures | Object | N.A | Object | MEP | IfcSwitchingDevice | POWEROUTLET | SGPset_SwitchingDevice | OutletType | Label | N.A | N.A | N.A
BCA | Family-Friendly Furniture | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *CHILDPROTECTIONSEAT | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Family-Friendly Furniture | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *DIAPERCHANGINGTABLE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Finishes | Material | Generic Models | Model Element | N.A | Object | ARC | IfcCovering | CLADDING | SGPset_Material | Material | Label | N.A | Name | N.A
SCDF | Finishes | Fire Rating | Generic Models | Model Element | N.A | Object | ARC | IfcCovering | *FIRECURTAIN | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A
SCDF | Finishes | Fire Rating | Floors | Slab | Slab | Slab | ARC | IfcCovering | FLOORING | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A
SCDF | Finishes | Material | Floors | Slab | Slab | Slab | ARC | IfcCovering | FLOORING | SGPset_Material | Material | Label | N.A | Name | N.A
NEA | Finishes | Material | Generic Models | Object | N.A | Object | ARC | IfcCovering | *PIPESLEEVE | SGPset_Material | Material | Label | N.A | Name | N.A
SCDF | Opening | Fire Access Opening | Void | Opening | N.A | Opening | ARC | IfcOpeningElement | Need not specify | SGPset_OpeningElement | FireAccessOpening | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *HOMEFIREALARMDEVICE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Foam Inlet | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | MEP | IfcFireSuppressionTerminal | *FOAMINLET | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Foam Outlet | N.A | Plumbing Fixtures | Pipe | N.A | Equipment | MEP | IfcFireSuppressionTerminal | *FOAMOUTLET | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Footing | Working Load DA1-2 | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FoundationStructuralLoad | WorkingLoad_DA1-2 | Integer | kN | N.A | 4321
NPARKS | Green Verge | Shrub Species | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | ShrubSpecies | Label | N.A | N.A | N.A
NPARKS | Green Verge | Approved Turf Species | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | ApprovedTurfSpecies | Label | N.A | N.A | N.A
BCA | Wall | Accreditation PAS (Precaster Accreditation Scheme) | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Slab | Accreditation PAS (Precaster Accreditation Scheme) | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Household Shelter | Construction Method | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystem | ConstructionMethod | Label | N.A | N.A | Precast
BCA | Household Shelter | Accreditation PAS (Precaster Accreditation Scheme) | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystem | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Household Shelter | Inner Dimensions | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystemDimension | InnerDimensions | Label | N.A | N.A | N.A
BCA | Household Shelter | Area | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystemDimension | Area | Area | m2 | N.A | N.A
BCA | Household Shelter | Height | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystemDimension | Height | Length | mm | N.A | N.A
BCA | Household Shelter | Wall Thickness | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystemDimension | WallThickness | Length | mm | N.A | N.A
BCA | Household Shelter | Slab Thickness | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *HOUSEHOLDSHELTER | SGPset_BuildingSystemDimension | SlabThickness | Length | mm | N.A | N.A
NPARKS | Landscape Plants | Reason For Removal | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | ReasonForRemoval | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Tree Number | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | TreeNumber | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Height | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElementDimension | Height | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Roadside | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | Roadside | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Lift | Lift Type | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElement | LiftType | Label | N.A | N | N.A
LTA | Parking Lot | Bicycle Rack Type | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxy | BicycleRack_Type | Label | N.A | N.A | Single Tier P Rack, Single Tier U Bar, Double Tier
BCA | Pipes / Drains | Pre-insulated | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE
BCA | Pipes / Drains | Construction Method | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | ConstructionMethod | Label | N.A | N.A | N.A
NPARKS | Pipes / Drains | Perforated | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | Perforated | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Pipes / Drains | Diameter | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
PUB | Pipes / Drains | Material | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Pipes / Drains | Gradient | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | Gradient | Label | N.A | N.A | N.A
PUB | Pipes / Drains | Length | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A
PUB | Pipes / Drains | Thickness | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegmentDimension | Thickness | Length | mm | N.A | N.A
NEA | Pipes / Drains | Trade Effluent | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE
BCA | Pipes / Drains | Pre-insulated | Flex Pipes | Pipe | N.A | Flexible Pipe | MEP | IfcPipeSegment | FLEXIBLESEGMENT | SGPset_PipeSegment | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE
BCA | Pipes / Drains | Construction Method | Flex Pipes | Pipe | N.A | Flexible Pipe | MEP | IfcPipeSegment | FLEXIBLESEGMENT | SGPset_PipeSegment | ConstructionMethod | Label | N.A | N.A | N.A
BCA | Pipes / Drains | Pre-insulated | Ducts | Duct | N.A | Duct | MEP | IfcDuctSegment | Need not specify | SGPset_DuctSegment | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE
BCA | Pipes / Drains | Construction Method | Ducts | Duct | N.A | Duct | MEP | IfcDuctSegment | Need not specify | SGPset_DuctSegment | ConstructionMethod | Label | N.A | N.A | N.A
BCA | Pipes / Drains | Pre-insulated | Duct Fittings | Duct Fitting | N.A | Duct Accessory | MEP | IfcDuctFitting | Need not specify | SGPset_DuctFitting | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE
BCA | Pipes / Drains | Construction Method | Duct Fittings | Duct Fitting | N.A | Duct Accessory | MEP | IfcDuctFitting | Need not specify | SGPset_DuctFitting | ConstructionMethod | Label | N.A | N.A | N.A
NEA | Pipes / Drains | Trade Effluent | Ducts | Duct | N.A | Duct | MEP | IfcDuctSegment | Need not specify | SGPset_DuctSegment | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE
NEA | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | *SCUPPERDRAIN | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | SPOOL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | *FLARESTACK | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | *RAINWATEROUTLET | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | Material | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | BEND | SGPset_Material | Material | Label | N.A | Name | N.A
NEA | Pipes / Drains | Nominal Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | BEND | SGPset_PipeFittingDimension | NominalDiameter | Length | mm | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *DRAINCHANNELBEND | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | ENTRY | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | EXIT | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *FLANGEADAPTOR | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *FLEXIBLECOUPLING | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | Material | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | JUNCTION | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | OBSTRUCTION | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | Material | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *PIPESILENCER | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *SHORTPIECE | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | Inner Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFittingDimension | InnerDiameter | Length | mm | N.A | N.A
NEA | Pipes / Drains | Nominal Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFittingDimension | NominalDiameter | Length | mm | N.A | N.A
PUB | Pipes / Drains | Outer Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFittingDimension | OuterDiameter | Length | mm | N.A | N.A
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Arsenic | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Barium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Barium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Beryllium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Beryllium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Biochemical Oxygen Demand | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_BiochemicalOxygenDemand | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Boron | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Boron | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Cadmium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Calcium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Calcium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Chemical Oxygen Demand | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_ChemicalOxygenDemand | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Chloride | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Chromium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Chromium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Colour | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Colour | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Copper | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Cyanide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Cyanide | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Detergent | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Detergent | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Grease And Oil | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_GreaseAndOil | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Iron | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Iron | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Lead | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Magnesium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Magnesium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Manganese | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Manganese | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Mercury | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Metals In Total | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_MetalsInTotal | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Nickel | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Nickel | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Nitrate | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Nitrate | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge PH Value | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_PHValue | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Phenolic Compound | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_PhenolicCompound | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Phosphate | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Phosphate | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Selenium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Selenium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Silver | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Silver | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Sulphate | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Sulphate | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Sulphide | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Temperature Of Discharge | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_TemperatureOfDischarge | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Tin | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Tin | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Total Dissolved Solid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_TotalDissolvedSolid | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Total Suspended Solid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_TotalSuspendedSolid | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Zinc | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Zinc | Label | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *PREFABRICATEDBATHROOMUNIT | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *PREFABRICATEDANDPREFINISHEDWALL | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *PREFABRICATEDANDPREFINISHEDFLOOR | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *PREFABRICATEDANDPREFINISHEDCEILING | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | ARC | IfcBuildingSystem | *PRECASTEXTERNALWALLWITHCASTINWINDOWS | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Model Groups | IFC Assignments | N.A | System | MEP | IfcBuildingSystem | *PREFABRICATEDPUMPSKID | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | Mechanical Connection Type | Model Groups | IFC Assignments | N.A | System | MEP | IfcBuildingSystem | *PREFABRICATEDMEPVERTICALMODULE | SGPset_BuildingSystem | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | Mechanical Connection Type | Model Groups | IFC Assignments | N.A | System | MEP | IfcBuildingSystem | *PREFABRICATEDMEPPLANTMODULE | SGPset_BuildingSystem | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | Mechanical Connection Type | Model Groups | IFC Assignments | N.A | System | MEP | IfcBuildingSystem | *PREFABRICATEDMEPHORIZONTALMODULE | SGPset_BuildingSystem | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | Is Common | Generic Models | Object | N.A | Object | MEP | IfcDiscreteAccessory | *PIPESUPPORT | SGPset_DiscreteAccessory | IsCommon | Boolean | N.A | N.A | TRUE/FALSE
PUB | System | N.A | Piping Systems | MEP System | N.A | System | External Works | IfcDistributionSystem | RAINWATER | N.A | N.A | N.A | N.A | N.A | N.A
NEA | System | Gradient | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | RAINWATER | SGPset_PipeSegmentDimension | Gradient | Label | N.A | N.A | N.A
LTA | Ramp | Material | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Material | Material | Label | N.A | N.A | TRUE/FALSE
BCA | Storey Shelter | Volume | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Volume | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | Litre | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | Litre | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A
` | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | Litre | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | Litre | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A
NEA | Refuse Handling Equipment | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSEBIN | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Road | Designed Vehicle Mass | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_CivilElement | DesignedVehicleMass | Real | N.A | N.A | 30 tonnes | New
LTA | Road | Material | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_Material | Material | Label | N.A | Name | N.A | New
LTA | Road | Road Category | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPSet_CivilElement | RoadCategory | Label | N.A | Name | N.A | New
PUB | RC Tank | Volume | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Volume | Label | N.A | N.A | N.A
BCA | Accessible Route | Width | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSIBLEROUTE | SGPset_SpaceDimension | Width | Length | mm | N.A | N.A
LTA | Road | N.A | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSPOINT | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Road | Height | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
LTA | Road | Material | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_Material | Material | Label | N.A | N.A | N.A
NParks | Roof | Construction Method | Roofs | Roof | N.A | Roof | ARC | IfcRoof | Need not specify | SGPset_Roof | ConstructionMethod | Label | N.A | N.A | N.A
NParks | Roof | Material | Roofs | Roof | N.A | Roof | ARC | IfcRoof | Need not specify | SGPset_Material | Material | Label | N.A | Name | N.A
NParks | Roof | Construction Method | Roofs | Slab | Slab | Slab | ARC | IfcSlab | ROOF | SGPset_Slab | ConstructionMethod | Label | N.A | N.A | N.A
NParks | Roof | Material | Roofs | Slab | Slab | Slab | ARC | IfcSlab | ROOF | SGPset_Material | Material | Label | N.A | Name | N.A
NParks | Roof | Construction Method | Roofs | Roof | N.A | Roof | ARC | IfcCovering | ROOFING | SGPset_Covering | ConstructionMethod | Label | N.A | N.A | N.A
NParks | Roof | Material | Roofs | Roof | N.A | Roof | ARC | IfcCovering | ROOFING | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Urinal | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
PUB | Water Closet | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
URA | Site Boundary | N.A | Topography | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *SITEBOUNDARY | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
BCA | Slab | Slab Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
BCA | Slab | Slab Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Slab | Slab Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | Type Designator | Label | N.A | N.A | N.A
BCA | Slab | Slab Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | LatticeGirderReinforcement | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Ambulant Disabled | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | AmbulantDisabled | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Children Friendly | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE
PUB | Space | C Value | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | CValue | Label | N.A | N.A | 0.45 - 1
SCDF | Space | Emergency Voice Communication System | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | EmergencyVoiceCommunicationSystem | Label | N.A | N.A | 1-way EVC System, 2-way EVC System, Public Address System
SCDF | Space | Fire Detection And Suppression System | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FireDetectionAndSuppressionSystem | Label | N.A | N.A | Automatic Fire Alarm System, Automatic Sprinkler System, Water Mist System, Video Image Fire Detector System, Kitchen Hood Fire Extinguishing System, Clean Agent Fire Extinguishing System, Automatic Foam Sprinkler System, Foam Extinguisher System
NParks | Space | Fully Covered With Tree Shrubs | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FullyCoveredWithTreesShrubs | Boolean | N.A | N.A | TRUE/FALSE
NEA | Space | Refuse Output | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | RefuseOutput | Real | N.A | N.A | 120, 200
SCDF | Space | Smoke Control System | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SmokeControlSystem | Label | N.A | N.A | Smoke Vent, Smoke Purging System, Ductless Jet Fan System, Engineered Smoke Control System
NEA | Space | Sound Power Level | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SoundPowerLevel | Label | N.A | N.A | N.A
NEA | Space | Sound Pressure Level | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SoundPressureLevel | Label | N.A | N.A | N.A
BCA | Space | Step Ramp Access | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | StepRampAccess | Boolean | N.A | N.A | TRUE/FALSE
BCA | Staircase | Accreditation PAS (Precaster Accreditation Scheme) | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Staircase | Mechanical Connection Type | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Staircase | Number of Treads | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | NumberOfTreads | Integer | N.A | N.A | N.A
PUB | System | Length | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DOMESTICCOLDWATER | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A
PUB | System | Material | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DOMESTICCOLDWATER | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DOMESTICCOLDWATER | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
PUB | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DRAINAGE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *FOAMFIREEXTINGUISHING | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *FOAMSPRINKLER | N.A | N.A | N.A | N.A | N.A | N.A
NEA | System | Trade Effluent | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | SEWAGE | SGPset_PipeSegment | TradeEffluent | N.A | N.A | N.A | N.A
PUB | Tank | Length | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Length | Length | mm | N.A | N.A
PUB | Tank | Width | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Width | Length | mm | N.A | N.A
PUB | Tank | Diameter | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Diameter | Length | mm | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | VESSEL | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Space | Is Potable | Areas | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | IsPotable | Boolean | N.A | N.A | TRUE/FALSE
PUB | Space | NominalCapacity | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | NominalCapacity | Real | N.A | N.A | N.A
PUB | Space | NominalCapacity | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | Thickness | Length | N.A | N.A | N.A
URA | Wall | N.A | Walls | Wall | Panel | Wall | ARC | IfcWall | RETAININGWALL | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Wall | Load Bearing | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Mechanical Connection Type | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Wall | Prefabricated Reinforcement Cage | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | PrefabricationReinforcementCage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Is Party Wall | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | IsPartyWall | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Is External | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | IsExternal | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Beam Façade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | BeamFacade | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Double Bay Façade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | Double Bay Façade | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Prefinished Façade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | Prefinished Façade | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Arrangement Type | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ArrangementType | Label | N.A | N.A | N.A
NEA | Waste Terminal | Trade Effluent | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | *WASTESUMP | SGPset_WasteTerminal | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE
URA | Window | Material | Windows | Window | N.A | Window | ARC | IfcWindow | Need not specify | SGPset_Material | Material | Label | N.A | Name | N.A
SCDF | Window | Safety Barrier Height | Windows | Window | N.A | Window | ARC | IfcWindow | Need not specify | SGPset_Window | SafetyBarrierHeight | Real | N.A | N.A | N.A