## README
This excel is a subset of the full IFC-SG mapping, and will be updated as CORENET X tech enablers (Collaboration Platform, Automated Model Checker) are developed
This excel is to be shared with industry practitioners and related partners involved in CORENET X
Using this excel:
1) | CORENET X Pilot Mapping: This provides details on the identified building component and the associated IFC representations to use
*Important: if IFC-SG Dimension parameter such as “Length, “Breadth” matches the native BIM object’s parameter, there is no need to declare the parameter in project, it will be exported automatically via the configuration files provided
2) | List of Space Parameter Values: Pls refer to the Space Values sheet
3) | Please read the change log tab for updates to the mapping
4) | The mapping is WIP, users to note that the mapping is not finalised
5) | For more info, please refer to the latest CORENET X Code of Practice:
https://go.gov.sg/cxcop

## Change Log
Date | Status | Topic | Description
2024-11-29 | Modify | All | Changes to align to the 2nd Edition of the CORENET X Code of Practice
2024-11-29 | Modify | Property | Space Values sheet added
2023-10-20 | Modify | All | Changes to align to the 1st Edition of the CORENET X Code of Practice
2023-07-02 | Modify | All | Changes to align to the Draft Release of the CORENET X Code of Practice
2023-05-12 | Modify | Property and unit | Capacity for Water Meter is changed to WaterUsagePerMonth with Unit m3/month
2023-05-12 | Modify | Unit | Capacity for Sump pump is changed from L to L/s
2023-05-05 | Modify | SubType | DOMESTICCOLDWATER changed to POTABLEWATER
2023-03-29 | Added | Property | Added Property "FireEmergencyVentilationMode" to IfcSpace
2023-03-10 | Modify | Property | URA updates on propertyname to be ACN_IsOpen24HrsToPublic
2023-02-28 | Removed | IP | Removed IP Children Friendly Properties for MEP disciplines for IC Child Urinal
2023-02-27 | Modify | Discipline | Replaced MEP Discipline to ARC for IC Platform lift
2023-02-27 | Modify | IP | IP "Location" term for Wet Riser, Dry Riser, Breeching Inlet, Hosereel, Standby Firehose, and Strobelight are not required as a separate property, thus removed the IP for clarity
2023-02-27 | Removed | Discipline | Removed ARC disciplines for Audio Alarms , ARC does not submit location of detectors & sensors in FSSD
2023-02-27 | Added | IC ,SubType, Property & Properties | URA updates IC : Area Strata Subtype: *AREA_STRATA Property : SGPset_SpaceArea_Strata Properties: AST_AreaType , AST_LegalArea , AST_Extg_StrataLotNumber , AST_Prop_StrataLotNumber, AST_AssociatedTo As per URA new excel (27th Feb Email Exchange)
2023-02-27 | Removed | IC ,SubType, Property & Properties | URA updates IC : Area Unit Subtype: *AREA_UNIT Property & Properties under : SGPset_SpaceArea_Unit As per URA new excel (27th Feb Email Exchange)
2023-02-27 | Modify | SubType | URA Updates - renamed *STRATALOT as per URA requested reps
2023-02-27 | Modify | Properties | Modified URA IC: Area GFA properties As per URA new excel (27th Feb Email Exchange)
2023-02-27 | Modify | Properties | Modified URA IC: Area Connectivity properties As per URA new excel (27th Feb Email Exchange)
2023-02-27 | Modify | Properties | Modified URA IC: Area Landscape properties As per URA new excel (27th Feb Email Exchange)
2023-02-27 | Removed | IC ,SubType, Property & Properties | URA updates: Removed existing specific areas, and to refer to the summary of areas URA has provided, for information to be submitted in the specified structures
2023-02-06 | Removed | IFC Entity | Removed IFC CivilElement for Road Verging, to use ifcSpace with SubTypes
2023-02-02 | Added | Discipline | added water closer, sink, shower, bell, strobelight, standby fire hose, hosereel and breeching inlet into ARC and MEP disciplines
2023-02-02 | Added | Discipline | added smokesensor, firesensor, heat detector, Dry Riser and Wet Riser into ARC and MEP disciplines
2023-02-01 | Added | Properties | added properties ComplyToPUBStandardDrawing and ReferToDrawingNumber
2023-02-01 | Removed | Properties | Grease Trap Length Height Width properties removed as details are in 2D drawings/standard design. PUB is requiring placeholder models to check for clashes with other objects
2023-02-01 | Removed | Properties | Height of Inspection Chamber removed, PUB checks for Depth, Top and invert level
2023-01-31 | Modify | Sandbox Addition | tagged R1 to SCDF PWD Systems (Speakers and Comms Devices and PWD Holding Point)
2023-01-17 | Added | Property | Added Deflection to IfcBeam
2023-01-05 | Modify | Revit Representation | Updated subtype LIFT's Revit Representation to Specialty Equipment
2022-12-23 | Modify | Discipline | Slab with Construction method is changed from ARC to STR domain discipline
2022-12-23 | Modify | Discipline | IC: Bedding disciplines changed from STR to External Works
2022-12-23 | Modify | Discipline | IC: Green Verge discipline changed from ARC to External Works
2022-12-23 | Added | Property | Added IntumescentPaintFireRating and EnclosureFireRating to SCDF Intumescent clause
2022-12-23 | Removed | Property | removed cable segment Fire Rating for clause on protected shaft used for enclosure of services
2022-12-23 | Removed | Property | Removed Fire Rating from IC Below: Cable Fitting Cable Segment Power Power Cable Pump Signal Cable Solar Panel Water Tank Window
2022-12-23 | Modify | IFC-SG Sub Type | IC: Smoke Engineering Air to ENGINEEREDSMOKECONTROLSYSTEM distributionSystem sub type
2022-12-23 | Added | IFC-SG Sub Type | Added system for SCDF SMOKECONTROL, SMOKEPURGING, SMOKEVENT, FIREEXTINGUISHING, FIREHYDRANT, SPRINKLER, HOSEREEL
2022-12-23 | Modify | IFC-SG Sub Type | IC: Sub Alarm Panel subtype ALARMPANEL to SUBALARMPANEL
2022-12-23 | Modify | IFC-SG Sub Type | IC: Main Alarm Panel subtype ALARMPANEL to MAINALARMPANEL
2022-12-23 | Removed | IFC | removed mapping from visual indicator as SCDF noted it is present in control panels, modeller need not model to such details
2022-12-23 | Modify | IFC-SG Sub Type | IC: Visual Alarm subtype updated to USERDEFINED STROBELIGHT
2022-12-21 | Added | Entity | added Accessway, Accessroad, FireEngineAccessway, FireEngineAccessroad, VehicularServiceRoad, Ingress, Egress with representation IfcSpace
2022-12-21 | Modify | Property | re-tag BCA structural requirements
2022-12-21 | Modify | Entity, Propertyset, SubType | modified PUB FOUNDATION from GeographicElement to PipeSegment (Tag to drains)
2022-12-21 | Modify | Domain, Discipline | Property WeldedMesh to be under STR instead of ARC
2022-12-21 | Modify | Domain, Discipline | Property LateralLoad to be under STR instead of ARC
2022-12-21 | Modify | PropertySet | SystemDimension changed to PipeSegmentDimension
2022-12-21 | Modify | IFC-SG Sub Type | subtype GRATING with properties AirTight and WaterTight was changed to INSPECTIONCHAMBERCOVER
2022-12-21 | Modify | IFC-SG Sub Type | IC: DetentionTank subtype STORAGE updated to DETENTIONTANK
2022-12-21 | Modify | Entity | SubType GONDOLA entity changed from BldgSystem to BEP
2022-12-21 | Modify | Property | Aligned IC: Water Tank (Potable Water) to same mapping as Water Tank with isPotable property
2022-12-20 | Modify | Property Set | Updated STR SGPset_Staircase to SGPset_Stair for alignment with ARC requirement
2022-12-20 | Modify | Property | all IP Material has SGPset_Material with property Material now
2022-12-11 | Modify | Property | Precast Stair MechanicalConnectionType label changed to HasMechanicalConnection boolean, ARC to STR discipline
2022-12-11 | Modify | Property Type | Flowrate data type update to Flow
2022-12-11 | Modify | Property Type | capacity data type update to volume
2022-12-08 | Modify | Data Unit | Aligned all Length Data Type to be in Unit "mm"
2022-12-08 | Modify | Property Units | Updated Nparks Girth and Height property unit from meters to mm
2022-12-07 | Removed | Property | URA Property HardscapeType
2022-12-07 | Modify | Property Set | URA SoftscapeType was changed to LandscapeType
2022-12-07 | Modify | Property | Update mapping for URA Area Schemes to refer to URA Excel (Sandbox) for Area Types: LANDSCAPE, CONNECTIVITY, UNIT and GFA
2022-12-05 | Removed | removed from mapping | Sandbox email from magdalene, nparks mentioned no need external planting Changed IC and IP to N.A
2022-12-05 | Modify | IFC-SG Sub Type | SCDF IC: Fire Sensor with object type SMOKEDETECTOR + SmokeDetectorType Property
2022-12-05 | Modify | Property | SCDF IC: Fire Sensor with object type SMOKEDETECTOR + SmokeDetectorType Property
2022-12-02 | Added | Property | IC: Blast Door to have Width and Height
2022-11-11 | Modify | Revit Representation | updated propose revit representation of "Accessway", "Accessroad", "Fire Engine Access Road", "Vehicular Service Road", "Ingress", "Egress" from "Room" to "Areas"
2022-11-07 | Modify | Entity | [Representation Relaxation] Updated Entity for Subtype "GONDOLA" from IfcBuildingSystem to IfcBuildingElementProxy
2022-11-07 | Modify | SubType | Updated IC: DetentionTank Subtype from "STORAGE" to "DETENTION" Removed property "IsPotable" for SubType "DETENTION"
2022-10-27 | Added | General | Added version number (date of modification) to the industry mapping
2022-10-27 | Modify | Properties | Cells in YELLOW for dimension properties to indicate automatic extractive from Native when export to IFC (Modellers no need to create extra dimension parameters for manual input)
2022-10-25 | Added | Object Type | Updated ACESSWAY, ACCESSROAD, FIREENGINEACCESSROAD, FIREENGINEACCESSWAY, VEHICULARSERVCEROAD, INGRESS, EGRESS as object types for IfcSpace, created as alternative representation for roads tagging for multi agencies road verging
2022-09-22 | Added | README Tab | readers to be informed that if dimension parameters (e.g. Length, Breadth) in mapping is the same as the native dimension parameters, there is no need to declare it again in the project, it will be handled via the export configurations
2022-09-22 | Modify | Revit Representation | updated propose revit representation of "Car lot", "Motor Cycle Lot" from "Generic Model" to "Parking"
2022-09-20 | Modify | IFC | Aligned IFC structures for URA GFA, LANDSCAPE, CONNECTIVITY, UNIT for reference to "URA EXCEL"
2022-09-15 | Modify | Property Set | Aligned "SGPset_Staircase" to "SGPset_Stair"
2022-09-15 | Modify | All | Consolidated URA Area Verging requirements into separate file: "URA Excel"
2022-09-08 | Added | Object Type | Added IfcSpace Object types for indication of road plans by multiple agencies, e.g. Accessway, Access Road, Fire Engine Accessway, Fire Engine Access Road, Vehicular Service Road, Ingress and Egress
2022-09-05 | Added | Property | Updated List of STR properties
2022-09-01 | Added | Property | ReferToDrawingNumber to STR members

## CX Pilot Mapping
Agency | Identified Component | Identified parameters | Revit Representation | Archicad Representation | Tekla Structures Representation | Bentley OpenBuildings Representation | Discipline | IFC4 Entities | IFC Sub Types (* = USERDEFINED) | Property Set | Property Name | Property Type | Property Unit | IFC4 Material Set | Sample Value for Reference
BCA | Accessible Route | Barrier Free Accessibility | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSIBLEROUTE | SGPset_BuildingElementProxy | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Accessible Route | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSIBLEROUTE | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
BCA | Accessible Route | Barrier Free Accessibility | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ACCESSIBLEROUTE | SGPset_CivilElement | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Accessible Route | Width | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ACCESSIBLEROUTE | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
BCA | Accessible Route | Barrier Free Accessibility | Ramps | Ramp | Item | Object | ARC | IfcRamp | *ACCESSIBLEROUTE | SGPset_Ramp | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Accessible Route | Width | Ramps | Ramp | Item | Object | ARC | IfcRamp | *ACCESSIBLEROUTE | SGPset_RampDimension | Width | Length | mm | N.A | N.A
BCA | Accessible Route | Barrier Free Accessibility | Floors | Slab | Slab | Slab | ARC | IfcSlab | *ACCESSIBLEROUTE | SGPset_Slab | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Accessible Route | Width | Floors | Slab | Slab | Slab | ARC | IfcSlab | *ACCESSIBLEROUTE | SGPset_SlabDimension | Width | Length | mm | N.A | N.A
BCA | Accessible Route | Barrier Free Accessibility | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSIBLEROUTE | SGPset_Space | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Beam | Beam Span Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | BeamSpanType | Label | N.A | N.A | Single, End, Interior, Cantilever
BCA | Beam | Bottom Left | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BottomLeft | Label | N.A | N.A | 3H25
BCA | Beam | Bottom Middle | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BottomMiddle | Label | N.A | N.A | 3H32+3H25+3H20
BCA | Beam | Bottom Right | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BottomRight | Label | N.A | N.A | 3H25
BCA | Beam | Construction Method | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Beam | Construction Method | Structural Framing | Beam | Beam | Beam | ARC | IfcBeam | Need not specify | SGPset_Beam | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Beam | Depth | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | Depth | Length | mm | N.A | 600
BCA | Beam | Left Connection Detail | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | LeftConnectionDetail | Label | N.A | N.A | Detail 1
BCA | Beam | Left Connection Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | LeftConnectionType | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Beam | Mark | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | Mark | Label | N.A | N.A | HB1, VB1, B1
BCA | Beam | Material Grade | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Beam | Mechanical Connection Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | MechanicalConnectionType | Label | N.A | N.A | Telescopic Beam Connector
BCA | Beam | Member Section | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | MemberSection | Label | N.A | N.A | RHS600x30x4, CHS500x3.0, 254x254x63 kg/m
BCA | Beam | Prefabrication Reinforcement Cage | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | PrefabricationReinforcementCage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Beam | ReferTo2DDetail | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Beam | Reinforcement Steel Grade | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Beam | Right Connection Detail | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | RightConnectionDetail | Label | N.A | N.A | Detail 1
BCA | Beam | Right Connection Type | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | RightConnectionType | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Beam | Section Fabrication Method | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | SectionFabricationMethod | Label | N.A | N.A | Hot rolled, Cold formed
BCA | Beam | Side Bar | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | SideBar | Label | N.A | N.A | H13-250
BCA | Beam | Splice Connection | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_SteelConnection | SpliceConnection | Label | N.A | N.A | Detail 3
BCA | Beam | Stirrups Left | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsLeft | Label | N.A | N.A | 4H13-300
BCA | Beam | Stirrups Middle | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsMiddle | Label | N.A | N.A | 4H13-300
BCA | Beam | Stirrups Right | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsRight | Label | N.A | N.A | 4H13-300
BCA | Beam | Stirrups Type Left | Structural Framing | Beam | Concrete Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsTypeLeft | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Beam | Stirrups Type Middle | Structural Framing | Beam | Concrete Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsTypeMiddle | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Beam | Stirrups Type Right | Structural Framing | Beam | Concrete Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | StirrupsTypeRight | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Beam | Top Left | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | TopLeft | Label | N.A | N.A | 3H32+3H25
BCA | Beam | Top Middle | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | TopMiddle | Label | N.A | N.A | 3H25
BCA | Beam | Top Right | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | TopRight | Label | N.A | N.A | 3H32+3H25
BCA | Beam | Width | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamDimension | Width | Length | mm | N.A | 300
BCA | Beam | Accreditation PAS (Precaster Accreditation Scheme) | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_Beam | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Beam | Beam Cage | Structural Framing | Beam | Beam | Beam | STR | IfcBeam | Need not specify | SGPset_BeamReinforcement | BeamCage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Borehole | Depth | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | Depth | Length | mm | N.A | 14560
BCA | Borehole | Mark | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | Mark | Label | N.A | N.A | BH1
BCA | Borehole | SHD Level SPT MoreThan 100N | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | SHDLevel_SPT_MoreThan_100N | Real | m | N.A | -27.5
BCA | Borehole | SHD Level SPT MoreThan 60N | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | SHDLevel_SPT_MoreThan_60N | Real | m | N.A | -15
BCA | Borehole | Termination Level | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | TerminationLevel | Real | m | N.A | -50.45
BCA | Borehole | Top Level | Generic Models | Object | N.A | Object | STR | IfcBuildingElementProxy | *BOREHOLE | SGPset_BuildingElementProxyDimension | TopLevel | Real | m | N.A | 1.8
SCDF | Breeching Inlet | Hose Nominal Diameter | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | MEP | IfcFireSuppressionTerminal | BREECHINGINLET | SGPset_FireSuppressionTerminal | Hose_NominalDiameter | Label | N.A | N.A | N.A
SCDF | Breeching Inlet | ID | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | MEP | IfcFireSuppressionTerminal | BREECHINGINLET | SGPset_FireSuppressionTerminal | ID | Label | N.A | N.A | N.A
SCDF | Breeching Inlet | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | ARC | IfcFireSuppressionTerminal | BREECHINGINLET | N.A | N.A | N.A | N.A | N.A | N.A
URA | Building Storey | N.A | Levels | Storey | N.A | Floor | ARC | IfcBuildingStorey | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Building Storey | Attic Level | Levels | Storey | N.A | Floor | ARC | IfcBuildingStorey | Need not specify | SGPset_BuildingStorey | AtticLevel | N.A | N.A | N.A | N.A
SCDF | Ceiling | Fire Rating | Ceilings | Ceiling | N.A | Slab | ARC | IfcCovering | CEILING | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A
SCDF | Ceiling | Material | Ceilings | Ceiling | N.A | Slab | ARC | IfcCovering | CEILING | SGPset_Material | Material | Label | N.A | Name | Sand, Corey Dust, Granite Dust, Gravel, Crusher Run, Recycled Aggregates, Intumescent Paint, Steel, Timber, Engineered Timber, Concrete, Wood, Brick, Reinforced Concrete, MET, Galvanized Mild Steel Heavy Duty, Plastic, Plastered, Fair-Faced Brickwall, Samples of Concrete Elements
BCA | Column | Accreditation PAS (Precaster Accreditation Scheme) | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Column | Arrangement Type | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_PrecastConcreteElementGeneral | ArrangementType | Label | N.A | N.A | Multi-Tier
BCA | Column | Breadth | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Breadth | Length | mm | N.A | 300
BCA | Column | Column Cage | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | ColumnCage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Column | Connection Details Bottom | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionDetailsBottom | Label | N.A | N.A | Detail 1
BCA | Column | Connection Details Top | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionDetailsTop | Label | N.A | N.A | Detail 1
BCA | Column | Connection Type Bottom | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionTypeBottom | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Column | Connection Type Top | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | ConnectionTypeTop | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Column | Construction Method | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Column | Construction Method | Columns | Column | Concrete Column | Column | ARC | IfcColumn | Need not specify | SGPset_Column | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Column | Diameter | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Diameter | Length | mm | N.A | 600
BCA | Column | End Storey | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | EndStorey | Label | N.A | N.A | 2nd Storey, Roof Storey
BCA | Column | Main Rebar | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | MainRebar | Label | N.A | N.A | 6H32+6H25
BCA | Column | Mark | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Mark | Label | N.A | N.A | TC1, C1
BCA | Column | Material Grade | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Column | Mechanical Connection Type | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | MechanicalConnectionType | Label | N.A | N.A | Column Shoes
BCA | Column | Member Section | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | MemberSection | Label | N.A | N.A | RHS600x30x4, CHS500x3.0, 254x254x63 kg/m
BCA | Column | Prefabricated Reinforcement Cage | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | PrefabricationReinforcementCage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Column | ReferTo2DDetail | Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Column | Reinforcement Steel Grade | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Column | Section Fabrication Method | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_Column | SectionFabricationMethod | Label | N.A | N.A | Hot rolled, Cold formed
BCA | Column | Splice Detail | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_SteelConnection | SpliceDetail | Label | N.A | N.A | Detail 3
BCA | Column | Starting Storey | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | StartingStorey | Label | N.A | N.A | 1st Storey, Lower Roof Storey
BCA | Column | Stirrups | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | Stirrups | Label | N.A | N.A | 4H13-300
BCA | Column | Stirrups Type | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Column | Width | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnDimension | Width | Length | mm | N.A | 600
BCA | Column | Working Load DA1-1 | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnStructuralLoad | WorkingLoad_DA1-1 | Integer | kN | N.A | 1234
BCA | Column | Working Load DA1-2 | Structural Columns | Column | Concrete Column | Column | STR | IfcColumn | Need not specify | SGPset_ColumnStructuralLoad | WorkingLoad_DA1-2 | Integer | kN | N.A | 1234
SCDF | Control Element | Purpose | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | CONTROLPANEL | SGPset_UnitaryControlElement | Purpose | Label | N.A | N.A | Main Panel, Sub Panel
NEA | Control Panel | Flushing | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | CONTROLPANEL | SGPset_UnitaryControlElement | PWCS_Flushing | Boolean | N.A | N.A | TRUE/FALSE
URA | Control Panel | N.A | Electrical Equipment | Flow Equipment | N.A | Equipment | MEP | IfcUnitaryControlElement | CONTROLPANEL | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Culvert | Load Bearing | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *CULVERT | SGPset_CivilElement | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Gradient | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CULVERT | SGPset_CivilElementDimension | Gradient | Label | N.A | N.A | N.A
PUB | Culvert | Diameter | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CULVERT | SGPset_CivilElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Culvert | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CULVERT | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Culvert | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CULVERT | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Culvert | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CULVERT | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Culvert | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CULVERT | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
LTA | Culvert | Footpath | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *CULVERT | SGPset_CivilElement | Footpath | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Material | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CULVERT | SGPset_Material | Material | Label | N.A | Name | N.A
NParks | Culvert | N.A | Generic Models | Object | Slab, Panel | Drains&Basins | ARC | IfcCivilElement | *ENTRANCECULVERT | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Culvert | Load Bearing | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *ENTRANCECULVERT | SGPset_CivilElement | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Gradient | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ENTRANCECULVERT | SGPset_CivilElementDimension | Gradient | Label | N.A | N.A | N.A
PUB | Culvert | Diameter | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ENTRANCECULVERT | SGPset_CivilElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Culvert | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ENTRANCECULVERT | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Culvert | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ENTRANCECULVERT | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Culvert | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ENTRANCECULVERT | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Culvert | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ENTRANCECULVERT | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
LTA | Culvert | Footpath | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *ENTRANCECULVERT | SGPset_CivilElement | Footpath | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Material | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ENTRANCECULVERT | SGPset_Material | Material | Label | N.A | Name | N.A
LTA | Culvert | Load Bearing | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *CROSSCULVERT | SGPset_CivilElement | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Gradient | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CROSSCULVERT | SGPset_CivilElementDimension | Gradient | Label | N.A | N.A | N.A
PUB | Culvert | Diameter | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CROSSCULVERT | SGPset_CivilElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Culvert | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CROSSCULVERT | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Culvert | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CROSSCULVERT | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Culvert | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CROSSCULVERT | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Culvert | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CROSSCULVERT | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
LTA | Culvert | Footpath | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *CROSSCULVERT | SGPset_CivilElement | Footpath | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Material | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *CROSSCULVERT | SGPset_Material | Material | Label | N.A | Name | N.A
LTA | Culvert | Load Bearing | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *EXTERNALDRAIN | SGPset_CivilElement | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Gradient | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *EXTERNALDRAIN | SGPset_CivilElementDimension | Gradient | Label | N.A | N.A | N.A
PUB | Culvert | Diameter | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *EXTERNALDRAIN | SGPset_CivilElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Culvert | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *EXTERNALDRAIN | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Culvert | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *EXTERNALDRAIN | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Culvert | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *EXTERNALDRAIN | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Culvert | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *EXTERNALDRAIN | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
LTA | Culvert | Footpath | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *EXTERNALDRAIN | SGPset_CivilElement | Footpath | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Material | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *EXTERNALDRAIN | SGPset_Material | Material | Label | N.A | Name | N.A
LTA | Culvert | Load Bearing | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *COMMONDRAIN | SGPset_CivilElement | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Gradient | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *COMMONDRAIN | SGPset_CivilElementDimension | Gradient | Label | N.A | N.A | N.A
PUB | Culvert | Diameter | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *COMMONDRAIN | SGPset_CivilElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Culvert | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *COMMONDRAIN | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Culvert | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *COMMONDRAIN | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Culvert | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *COMMONDRAIN | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Culvert | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *COMMONDRAIN | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
LTA | Culvert | Footpath | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *COMMONDRAIN | SGPset_CivilElement | Footpath | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Material | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *COMMONDRAIN | SGPset_Material | Material | Label | N.A | Name | N.A
LTA | Culvert | Load Bearing | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *INTERNALDRAIN | SGPset_CivilElement | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Gradient | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *INTERNALDRAIN | SGPset_CivilElementDimension | Gradient | Label | N.A | N.A | N.A
PUB | Culvert | Diameter | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *INTERNALDRAIN | SGPset_CivilElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Culvert | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *INTERNALDRAIN | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Culvert | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *INTERNALDRAIN | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Culvert | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *INTERNALDRAIN | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Culvert | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *INTERNALDRAIN | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
LTA | Culvert | Footpath | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *INTERNALDRAIN | SGPset_CivilElement | Footpath | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Material | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *INTERNALDRAIN | SGPset_Material | Material | Label | N.A | Name | N.A
LTA | Culvert | Load Bearing | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *OUTLETDRAIN | SGPset_CivilElement | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Gradient | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *OUTLETDRAIN | SGPset_CivilElementDimension | Gradient | Label | N.A | N.A | N.A
PUB | Culvert | Diameter | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *OUTLETDRAIN | SGPset_CivilElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Culvert | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *OUTLETDRAIN | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Culvert | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *OUTLETDRAIN | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Culvert | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *OUTLETDRAIN | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Culvert | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *OUTLETDRAIN | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
LTA | Culvert | Footpath | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *OUTLETDRAIN | SGPset_CivilElement | Footpath | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Material | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *OUTLETDRAIN | SGPset_Material | Material | Label | N.A | Name | N.A
LTA | Culvert | Load Bearing | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *ROADSIDEDRAIN | SGPset_CivilElement | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Gradient | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ROADSIDEDRAIN | SGPset_CivilElementDimension | Gradient | Label | N.A | N.A | N.A
PUB | Culvert | Diameter | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ROADSIDEDRAIN | SGPset_CivilElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Culvert | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ROADSIDEDRAIN | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Culvert | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ROADSIDEDRAIN | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Culvert | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ROADSIDEDRAIN | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Culvert | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ROADSIDEDRAIN | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
LTA | Culvert | Footpath | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *ROADSIDEDRAIN | SGPset_CivilElement | Footpath | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Material | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *ROADSIDEDRAIN | SGPset_Material | Material | Label | N.A | Name | N.A
LTA | Culvert | Load Bearing | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *TRENCH | SGPset_CivilElement | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Gradient | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *TRENCH | SGPset_CivilElementDimension | Gradient | Label | N.A | N.A | N.A
PUB | Culvert | Diameter | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *TRENCH | SGPset_CivilElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Culvert | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *TRENCH | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Culvert | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *TRENCH | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Culvert | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *TRENCH | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Culvert | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *TRENCH | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
LTA | Culvert | Footpath | Generic Models | Object | Slab, Panel | Drains&Basins | STR | IfcCivilElement | *TRENCH | SGPset_CivilElement | Footpath | Boolean | N.A | N.A | TRUE/FALSE
PUB | Culvert | Material | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | *TRENCH | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Culvert | N.A | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcBuildingElementProxy | *DROPINLETCHAMBER | N.A | N.A | N.A | N.A | N.A | N.A
URA | Curtain Wall | N.A | Curtain Systems | Curtain Wall | N.A | Curtain Wall | ARC | IfcCurtainWall | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Damper | Fire Rating | Duct Accessories | Object | N.A | Object | MEP | IfcDamper | FIREDAMPER | SGPset_Damper | FireRating | Label | hr | N.A | 30min, 60min, 90min, 120min, 150min, 180min, 210min, 240min
SCDF | Damper | Fire Rating | Duct Accessories | Object | N.A | Object | MEP | IfcDamper | FIRESMOKEDAMPER | SGPset_Damper | FireRating | Label | hr | N.A | 30min, 60min, 90min, 120min, 150min, 180min, 210min, 240min
SCDF | Damper | Fire Rating | Duct Accessories | Object | N.A | Object | MEP | IfcDamper | SMOKEDAMPER | SGPset_Damper | FireRating | Label | hr | N.A | 30min, 60min, 90min, 120min, 150min, 180min, 210min, 240min
PUB | Distribution Chamber | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Distribution Chamber | Depth | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Depth | Length | mm | N.A | N.A
PUB | Distribution Chamber | Height | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Height | Length | mm | N.A | N.A
PUB | Distribution Chamber | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Length | Length | mm | N.A | N.A
PUB | Distribution Chamber | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElementDimension | Width | Length | mm | N.A | N.A
PUB | Distribution Chamber | Material | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Distribution Chamber | ID | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | SGPset_DistributionChamberElement | ID | Label | N.A | Name | N.A
PUB | Distribution Chamber | Status | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | INSPECTIONCHAMBER | Pset_DistributionChamberElementCommon | Status | Label | N.A | Name | Temporary, Demolished, Existing, Proposed, To Be Removed, To Be Transplanted, Abandoned, New
PUB | Distribution Chamber | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Distribution Chamber | Depth | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElementDimension | Depth | Length | mm | N.A | N.A
PUB | Distribution Chamber | Material | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Distribution Chamber | ID | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | SGPset_DistributionChamberElement | ID | Label | N.A | Name | N.A
PUB | Distribution Chamber | Status | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | MANHOLE | Pset_DistributionChamberElementCommon | Status | Label | N.A | Name | Temporary, Demolished, Existing, Proposed, To Be Removed, To Be Transplanted, Abandoned, New
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Distribution Chamber | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Distribution Chamber | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Diameter | Length | mm | N.A | N.A
PUB | Distribution Chamber | Depth | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Depth | Length | mm | N.A | N.A
PUB | Distribution Chamber | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Length | Length | mm | N.A | N.A
PUB | Distribution Chamber | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElementDimension | Width | Length | mm | N.A | N.A
PUB | Distribution Chamber | Material | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Distribution Chamber | ID | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | SGPset_DistributionChamberElement | ID | Label | N.A | Name | N.A
PUB | Distribution Chamber | Status | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | SUMP | Pset_DistributionChamberElementCommon | Status | Label | N.A | Name | Temporary, Demolished, Existing, Proposed, To Be Removed, To Be Transplanted, Abandoned, New
PUB | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | METERCHAMBER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *SCREENCHAMBER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | TRENCH | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *PWCSINSPECTIONCHAMBER | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *PWCSMANHOLE | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Distribution Chamber | N.A | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcDistributionChamberElement | *SAMPLINGSUMP | SGPset_DistributionChamberElement | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE
NEA | Distribution Chamber | External Reference | Generic Models | Covering | N.A | Slab | ARC | IfcCovering | *PWCSMANHOLECOVER | SGPset_Covering | ExternalReference | Label | N.A | N.A | SS 30 Manhole Tops and Surface-box Tops
NEA | Distribution Chamber | Watertight | Generic Models | Covering | N.A | Slab | ARC | IfcCovering | *PWCSMANHOLECOVER | SGPset_Covering | Watertight | Boolean | N.A | N.A | TRUE/FALSE
NEA | Distribution Chamber | Watertight | Generic Models | Covering | N.A | Slab | ARC | IfcCovering | *PWCSINSPECTIONCHAMBERCOVER | SGPset_Covering | Watertight | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | Clear Height | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | ClearHeight | Length | mm | N.A | N.A
SCDF | Door | Clear Width | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | ClearWidth | Length | mm | N.A | N.A
SCDF | Door | Fire Exit | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | Pset_DoorCommon | FireExit | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | Pset_DoorCommon | FireRating | Label | hr | N.A | ½-hr , 1-hr
SCDF | Door | Fire Access Opening | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | FireAccessOpening | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | Hardware | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | Hardware | Boolean | N.A | N.A | TRUE/FALSE
NEA | Door | Main Entrance | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | MainEntrance | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | One Way Locking Device | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | OneWayLockingDevice | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | Operation Type | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | OperationType | Label | N.A | N.A | N.A
BCA | Door | Overall Width | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_DoorDimension | OverallWidth | Length | mm | N.A | N.A
BCA | Door | Thickness | Doors | Door | N.A | Door | ARC | IfcDoor | *BLASTDOOR | SGPset_DoorDimension | Thickness | Length | mm | N.A | N.A
BCA | Door | PowerOperated | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | PowerOperated | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | Self Closing | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | SelfClosing | Boolean | N.A | N.A | TRUE/FALSE
BCA | Door | Vision Panel | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Door | VisionPanel | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Door | Material | Doors | Door | N.A | Door | ARC | IfcDoor | Need not specify | SGPset_Material | Material | Label | N.A | Name | N.A
SCDF | Door | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | *ROLLERSHUTTER | Pset_DoorCommon | FireRating | Label | hr | N.A | N.A
SCDF | Door | Operation Type | Doors | Door | N.A | Door | ARC | IfcDoor | *ROLLERSHUTTER | SGPset_Door | OperationType | Label | N.A | N.A | N.A
URA | Earthworks | Area | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *EXISTINGEARTHWORKS | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
URA | Earthworks | Area | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PROPOSEDEARTHWORKS | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
URA | Earthworks | Area | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | TERRAIN | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
BCA | Escalator | N.A | Mechanical Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | ESCALATOR | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Family-Friendly Furniture | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *CHANGINGBED | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Family-Friendly Furniture | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *CHILDPROTECTIONSEAT | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Family-Friendly Furniture | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *DIAPERCHANGINGTABLE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Finishes | Fire Rating | Floors | Slab | Slab | Slab | ARC | IfcCovering | FLOORING | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A
SCDF | Finishes | Material | Floors | Slab | Slab | Slab | ARC | IfcCovering | FLOORING | SGPset_Material | Material | Label | N.A | Name | N.A
SCDF | Finishes | Material | Generic Models | Model Element | N.A | Object | ARC | IfcCovering | CLADDING | SGPset_Material | Material | Label | N.A | Name | N.A
SCDF | Finishes | Fire Rating | Generic Models | Model Element | N.A | Object | ARC | IfcCovering | *FIRECURTAIN | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A
NEA | Finishes | Material | Generic Models | Object | N.A | Object | ARC | IfcCovering | *PIPESLEEVE | SGPset_Material | Material | Label | N.A | Name | N.A
BCA | Finishes | N.A | Generic Models | Model Element | N.A | Object | ARC | IfcBuildingElementProxy | *TACTILETILE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Fire Access Opening | Fire Access Opening | Void, Shaft Openings | Opening | N.A | Opening |  | IfcOpeningElement | OPENING | SGPset_OpeningElement | FireAccessOpening | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Fire Access Opening | Fire Access Opening | Doors | Door | N.A | Door | ARC | IfcDoor | *OPENING | SGPset_Door | FireAccessOpening | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Fire Access Opening | Fire Access Opening | Windows | Window | N.A | Window | ARC | IfcWindow | *OPENING | SGPset_Window | FireAccessOpening | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *FIREALARMPANEL | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | ARC | IfcAlarm | *MANUALALARMCALLPOINT | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *VISUALALARM | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *SOUNDER | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Fire Alarm | N.A | Fire Alarm Devices | Object | N.A | Solid | MEP | IfcAlarm | *HOMEFIREALARMDEVICE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Fire Extinguisher | Fire Extinguisher Rating | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *PORTABLEFIREEXTINGUISHER | SGPset_BuildingElementProxy | FireExtinguisherRating | Label | N.A | N.A | 70B
SCDF | Fire Hydrant | ID | Plumbing Fixtures | Object | N.A | Fire Protection | MEP | IfcFireSuppressionTerminal | FIREHYDRANT | SGPset_FireSuppressionTerminal | ID | Label | N.A | N.A | N.A
SCDF | Fire Hydrant | Private | Plumbing Fixtures | Object | N.A | Fire Protection | MEP | IfcFireSuppressionTerminal | FIREHYDRANT | SGPset_FireSuppressionTerminal | Private | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Fire Hydrant | Public | Plumbing Fixtures | Object | N.A | Fire Protection | MEP | IfcFireSuppressionTerminal | FIREHYDRANT | SGPset_FireSuppressionTerminal | Public | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Foam Inlet | N.A | Plumbing Fixtures | Pipe Flow Terminal | N.A | Equipment | MEP | IfcFireSuppressionTerminal | *FOAMINLET | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Foam Outlet | N.A | Plumbing Fixtures | Pipe | N.A | Equipment | MEP | IfcFireSuppressionTerminal | *FOAMOUTLET | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Footpath | N.A | [5 empty] | IfcBuildingElementProxy | *TACTILETILE | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Footpath | Material | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *FOOTPATH | SGPset_Material | Material | Label | N.A | Name | N.A
BCA | Footpath | Width | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *FOOTPATH | SGPset_CivilElementDimension | Width | Length | N.A | N.A | N.A
BCA | Footing | DA1-1 Bearing Capacity | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | DA1-1_BearingCapacity | Integer | kPa | N.A | 150
BCA | Footing | DA1-2 Bearing Capacity | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | DA1-2_BearingCapacity | Integer | kPa | N.A | 120
BCA | Footing | ReferTo2DDetail | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Footing | Reinforcement Steel Grade | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Footing | Soil Verification Test | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Footing | SoilVerificationTest | Label | N.A | N.A | 2 nos plate load Test
BCA | Footing | Breadth | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Breadth | Length | mm | N.A | 6200
BCA | Footing | Depth | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Depth | Length | mm | N.A | 300
BCA | Footing | Mark | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Mark | Label | N.A | N.A | F2, PC1, PC2, PC4_1
BCA | Footing | Width | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingDimension | Width | Length | mm | N.A | 300
BCA | Footing | Bottom Distribution | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | BottomDistribution | Label | N.A | N.A | H16-150
BCA | Footing | Bottom Main | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | BottomMain | Label | N.A | N.A | H25-150
BCA | Footing | Side Bar | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | SideBar | Label | N.A | N.A | H13-250
BCA | Footing | Stirrups | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | Stirrups | Label | N.A | N.A | H13-200-300
BCA | Footing | Stirrups Type | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Footing | Top Distribution | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | TopDistribution | Label | N.A | N.A | H16-150
BCA | Footing | Top Main | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FootingReinforcement | TopMain | Label | N.A | N.A | H25-150
BCA | Footing | Working Load DA1-1 | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FoundationStructuralLoad | WorkingLoad_DA1-1 | Integer | kN | N.A | 4321
BCA | Footing | Working Load DA1-2 | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_FoundationStructuralLoad | WorkingLoad_DA1-2 | Integer | kN | N.A | 4321
BCA | Footing | Material Grade | Structural Foundations | Footing | Concrete Footing | Footing | STR | IfcFooting | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
PUB | Grating | N.A | Generic Models | Covering | N.A | Object | ARC | IfcDiscreteAccessory | *GRATING | N.A | N.A | N.A | N.A | N.A | N.A
NPARKS | Green Verge | Approved Soil Mixture | Toposolid | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Green Verge | Approved Turf Species | Toposolid | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | ApprovedTurfSpecies | Label | N.A | N.A | N.A
NPARKS | Green Verge | Area | Toposolid | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
NPARKS | Green Verge | Shrub Species | Toposolid | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | ShrubSpecies | Label | N.A | N.A | N.A
NPARKS | Green Verge | Shrubs | Toposolid | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *GREENVERGE | SGPset_GeographicElement | Shrubs | Label | N.A | N.A | N.A
NEA | Gutter | N.A | Plumbing Fixtures | Pipe | N.A | Drains&Basins | MEP | IfcPipeSegment | GUTTER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Gutter | Construction Method | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElement | ConstructionMethod | Label | N.A | N.A | N.A
PUB | Gutter | Height | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
PUB | Gutter | Length | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Length | Length | mm | N.A | N.A
PUB | Gutter | Thickness | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
PUB | Gutter | Width | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElementDimension | Width | Length | mm | N.A | N.A
PUB | Gutter | Public | Generic Models | Object | Slab, Panel | Drains&Basins | MEP | IfcCivilElement | GUTTER | SGPset_CivilElement | Public | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Hose Reel | Hose Nominal Diameter | Mechanical Equipment | Pipe Flow Terminal | N.A | Fixture | MEP | IfcFireSuppressionTerminal | HOSEREEL | SGPset_FireSuppressionTerminal | Hose_NominalDiameter | Label | mm | N.A | N.A
SCDF | Hose Reel | Hose Nominal Diameter | Mechanical Equipment | Pipe | N.A | Pipe | MEP | IfcFireSuppressionTerminal | *STANDBYFIREHOSE | SGPset_FireSuppressionTerminal | Hose_NominalDiameter | Label | mm | N.A | N.A
BCA | Household Shelter | N.A | [5 empty] | IfcSpace | *HSSETBACK | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Household Shelter | N.A | Lighting Fixtures | Object | N.A | Object | ARC | IfcLightFixture | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Household Shelter | N.A | Electrical Equipment, Communication Devices, Electrical Fixtures | Flow Equipment, Object | N.A | Equipment, Object | ARC | IfcOutlet | COMMUNICATIONSOUTLET | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Household Shelter | N.A | Electrical Equipment, Communication Devices, Electrical Fixtures | Flow Equipment, Object | N.A | Equipment, Object | ARC | IfcOutlet | DATAOUTLET | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Household Shelter | N.A | Electrical Equipment, Communication Devices, Electrical Fixtures | Flow Equipment, Object | N.A | Equipment, Object | ARC | IfcOutlet | POWEROUTLET | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Household Shelter | N.A | Electrical Fixtures, Specialty Equipment, Lighting Devices | Object | N.A | Object | ARC | IfcSwitchingDevice | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Household Shelter | Internal Length | Areas | Zone | N.A | Space | ARC | IfcSpace | SPACE | SGPset_SpaceDimension | InternalLength | Length | mm | N.A | N.A
BCA | Household Shelter | Internal Width | Areas | Zone | N.A | Space | ARC | IfcSpace | SPACE | SGPset_SpaceDimension | InternalWidth | Length | mm | N.A | N.A
BCA | Household Shelter | Construction Method | Areas | Zone | N.A | Space | ARC | IfcSpace | SPACE | SGPset_Space | ConstructionMethod | Label | N.A | N.A | Precast
PUB | Interceptor | Comply to PUB Standard Drawing | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_Interceptor | ComplyToPUBStandardDrawing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Interceptor | Refer to Drawing Number | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_Interceptor | ReferToDrawingNumber | Label | N.A | N.A | N.A
PUB | Interceptor | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Height | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | Height | Length | N.A | N.A | N.A
PUB | Interceptor | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | Length | Length | N.A | N.A | N.A
PUB | Interceptor | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | GREASE | SGPset_InterceptorDimension | Width | Length | N.A | N.A | N.A
PUB | Interceptor | Comply to PUB Standard Drawing | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_Interceptor | ComplyToPUBStandardDrawing | Boolean | N.A | N.A | TRUE/FALSE
PUB | Interceptor | Refer to Drawing Number | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_Interceptor | ReferToDrawingNumber | Label | N.A | N.A | N.A
PUB | Interceptor | Invert Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | InvertLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Top Level | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | TopLevel | Label | N.A | N.A | N.A
PUB | Interceptor | Diameter | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Diameter | Length | N.A | N.A | N.A
PUB | Interceptor | Height | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Height | Length | N.A | N.A | N.A
PUB | Interceptor | Length | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Length | Length | N.A | N.A | N.A
PUB | Interceptor | Width | Plumbing Fixtures | Flow Equipment | N.A | Equipment | MEP | IfcInterceptor | OIL | SGPset_InterceptorDimension | Width | Length | N.A | N.A | N.A
| Lamp Post | N.A | [5 empty] | IfcCivilElement | *LAMPPOST | N.A | N.A | N.A | N.A | N.A | N.A
NPARKS | Landscape Plants | Reason For Removal | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | ReasonForRemoval | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Species | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | Species | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Status | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | Status | Label | N.A | N.A | To be retained, To be felled/removed, To be transplanted, To be planted/proposed/new
NPARKS | Landscape Plants | Tree Number | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | TreeNumber | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Tree Size | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | TreeSize | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Girth | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElementDimension | Girth | Length | mm | N.A | N.A
NPARKS | Landscape Plants | Height | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElementDimension | Height | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Roadside | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | Roadside | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Landscape Plants | Single Stem | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_TREE | SGPset_GeographicElement | SingleStem | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Landscape Plants | Reason For Removal | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | ReasonForRemoval | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Species | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | Species | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Status | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | Status | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Tree Number | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | TreeNumber | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Tree Size | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | TreeSize | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Girth | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElementDimension | Girth | Length | mm | N.A | N.A
NPARKS | Landscape Plants | Height | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElementDimension | Height | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Single Stem | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_PALM | SGPset_GeographicElement | SingleStem | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Landscape Plants | Species | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_SHRUBS | SGPset_GeographicElement | Species | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Status | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_SHRUBS | SGPset_GeographicElement | Status | Label | N.A | N.A | N.A
NPARKS | Landscape Plants | Turf | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_SHRUBS | SGPset_GeographicElement | Turf | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Landscape Plants | Approved Soil Mixture | Planting | Object | N.A | Object | ARC | IfcGeographicElement | *LANDSCAPE_EXTERNALPLANTING | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
BCA | Lift | Barrier Free Accessibility | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElement | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Lift | Length | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | Length | Length | mm | N.A | N.A
BCA | Lift | Width | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | Width | Length | mm | N.A | N.A
SCDF | Lift | Clear Depth | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | ClearDepth | Length | mm | N.A | N.A
SCDF | Lift | Clear Height | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | ClearHeight | Length | mm | N.A | N.A
SCDF | Lift | Clear Width | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElementTypeLiftDimension | ClearWidth | Length | mm | N.A | N.A
SCDF | Lift | Fire Fighting Lift | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElement | FireFightingLift | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Lift | Lift Type | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *LIFT | SGPset_TransportElement | LiftType | Label | N.A | N | N.A
BCA | Lift | Length | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *CARLIFT | SGPset_TransportElementTypeLiftDimension | Length | Length | mm | N.A | N.A
BCA | Lift | Width | Specialty Equipment | Transport Element | N.A | Equipment | ARC | IfcTransportElement | *CARLIFT | SGPset_TransportElementTypeLiftDimension | Width | Length | mm | N.A | N.A
BCA | Parking Lot | Barrier Free Accessibility | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Car Parking Served By Car Lift | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | CarParking_ServedByCarLift | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Mechanised Parking System | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | MechanisedParkingSystem | Boolean | N.A | N.A | TRUE/FALSE
BCA | Parking Lot | Family Parking Lot | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | FamilyLot | Boolean | N.A | N.A | TRUE/FALSE
BCA | Parking Lot | Length | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
BCA | Parking Lot | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Lot Number | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | LotNumber | Label | N.A | N.A | N.A
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *MOTOR-CYCLELOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Parking Use | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | ParkingUse | Label | N.A | N.A | Electric Vehicle, Oil Tanker, Buggy, Vacuum Truck, Mobile Tanker
LTA | Parking Lot | Vehicle Type | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LORRYLOT | SGPset_BuildingElementProxy | VehicleType | Label | N.A | N.A | Rigid-framed vehicle
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *COACHLOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ARTICULATEDVEHICLELOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ARTICULATEDVEHICLELOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
NPARKS | Parking Lot | Open At Grade | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ARTICULATEDVEHICLELOT | SGPset_BuildingElementProxy | OpenAtGrade | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Parking Lot | Perforated | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ARTICULATEDVEHICLELOT | SGPset_BuildingElementProxy | Perforated | Boolean | N.A | N.A | TRUE/FALSE
LTA | Parking Lot | Bicycle Lot Count | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxy | BicycleLotCount | Integer | N.A | N.A | Limited to 1 or 2 only
LTA | Parking Lot | Bicycle Rack Type | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxy | BicycleRack_Type | Label | N.A | N.A | Single Tier P Rack, Single Tier U Bar, Double Tier
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *BICYCLELOT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOBBY | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *CARLOBBY | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *HOLDINGBAY | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *HOLDINGBAY | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Parking Lot | Length | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *QUEUINGSPACE | SGPset_BuildingElementProxyDimension | Length | Length | mm | N.A | N.A
LTA | Parking Lot | Width | Parking | Object | N.A | Object | ARC | IfcBuildingElementProxy | *QUEUINGSPACE | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
BCA | Pile | Borehole Ref | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | BoreholeRef | Label | N.A | N.A | BH2, BH3, BH12-2
BCA | Pile | Breadth | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Breadth | Length | mm | N.A | 300
BCA | Pile | Construction Method | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC, Spun
BCA | Pile | CutOffLevel_SHD | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | CutOffLevel_SHD | Real | m | N.A | -1.35
BCA | Pile | DA1-1 Compression Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-1_CompressionCapacity | Integer | kN | N.A | 5683
BCA | Pile | DA1-1 Compression Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-1_CompressionDesignLoad | Integer | kN | N.A | 5515
BCA | Pile | DA1-1 Tension Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-1_TensionCapacity | Integer | kN | N.A | 3655
BCA | Pile | DA1-1 Tension Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-1_TensionDesignLoad | Integer | kN | N.A | 3255
BCA | Pile | DA1-2 Compression Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-2_CompressionCapacity | Integer | kN | N.A | 4823
BCA | Pile | DA1-2 Compression Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-2_CompressionDesignLoad | Integer | kN | N.A | 4650
BCA | Pile | DA1-2 Tension Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | DA1-2_TensionCapacity | Integer | kN | N.A | 3025
BCA | Pile | DA1-2 Tension Design Load | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | DA1-2_TensionDesignLoad | Integer | kN | N.A | 2850
BCA | Pile | Diameter | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Diameter | Length | mm | N.A | 600
BCA | Pile | Length | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Length | Length | mm | N.A | 40000
BCA | Pile | Main Rebar | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | MainRebar | Label | N.A | N.A | 10H32+10H16
BCA | Pile | Mark | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Mark | Label | N.A | N.A | P156
BCA | Pile | Material Grade | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Pile | Member Section | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | MemberSection | Label | N.A | N.A | CHS500x3.0, 254x254x63 kg/m
BCA | Pile | Min Embedment Into Bearing Layer SPT More Than 100 N | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | MinEmbedmentIntoBearingLayer_SPT_MoreThan_100N | Real | m | N.A | 16.5
BCA | Pile | Min Embedment Into Bearing Layer SPT More Than 60 N | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | MinEmbedmentIntoBearingLayer_SPT_MoreThan_60N | Real | m | N.A | 23.2
BCA | Pile | Min Rock Socketing Length | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | MinRockSocketingLength | Real | m | N.A | 16.5
BCA | Pile | Negative Skin Friction | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileStructuralLoad | NegativeSkinFriction | Integer | kN | N.A | 135
BCA | Pile | Pile Type | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | PileType | Label | N.A | N.A | Driven, Bored, Jacked in
BCA | Pile | Reinforcement Length | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | ReinforcementLength | Label | m | N.A | Fully reinforced, Unreinforced, 12, 18, 24, 30, 36
BCA | Pile | Reinforcement Steel Grade | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Pile | Stirrups | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileReinforcement | Stirrups | Label | N.A | N.A | 1H16-250
BCA | Pile | Structural Compression Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | StructuralCompressionCapacity | Integer | kN | N.A | 6525
BCA | Pile | Structural Tension Capacity | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_Pile | StructuralTensionCapacity | Integer | kN | N.A | 3825
BCA | Pile | ToeLevel_SHD | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | ToeLevel_SHD | Real | m | N.A | -63.35
BCA | Pile | Width | Structural Foundations | Object | Concrete Column | Base Plate | STR | IfcPile | Need not specify | SGPset_PileDimension | Width | Length | mm | N.A | 600
BCA | Pile | End Bearing R4 Design Factor | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | EndBearingR4DesignFactor | Real | N.A | N.A
BCA | Pile | No Of Non Destructive Test Pile | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfNonDestructiveTestPile | Integer | N.A | N.A | 8
BCA | Pile | No of ULT Test | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfULTTest | Integer | N.A | N.A | 2
BCA | Pile | No of Working Load Test - Maintained Load Test | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfWorkingLoadTest_MaintainedLoadTest | Integer | N.A | N.A | 3
BCA | Pile | No of Working Load Test - Rapid Load Test | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | NoOfWorkingLoadTest_RapidLoadTest | Integer | N.A | N.A | 3
BCA | Pile | Pile Model Factor | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | PileModelFactor | Real | N.A | N.A | 1.35 / 1.55
BCA | Pile | Shaft R4 Design Factor | Project Information | IFC Project Manager | N.A | Floor Manager | STR | IfcBuilding | Need not specify | SGPset_PilingDesignParameter | ShaftR4DesignFactor | Real | N.A | N.A
BCA | Pipes / Drains | Construction Method | Flex Pipes | Pipe | N.A | Flexible Pipe | MEP | IfcPipeSegment | FLEXIBLESEGMENT | SGPset_PipeSegment | ConstructionMethod | Label | N.A | N.A | N.A
BCA | Pipes / Drains | Pre-insulated | Flex Pipes | Pipe | N.A | Flexible Pipe | MEP | IfcPipeSegment | FLEXIBLESEGMENT | SGPset_PipeSegment | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE
BCA | Pipes / Drains | Construction Method | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | ConstructionMethod | Label | N.A | N.A | N.A
PUB | Pipes / Drains | Inner Diameter | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegmentDimension | InnerDiameter | Length | mm | N.A | N.A
PUB | Pipes / Drains | Gradient | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | Gradient | Label | N.A | N.A | N.A
PUB | Pipes / Drains | Length | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A
PUB | Pipes / Drains | Material | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_Material | Material | Label | N.A | Name | N.A
NPARKS | Pipes / Drains | Perforated | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | Perforated | Boolean | N.A | N.A | TRUE/FALSE
BCA | Pipes / Drains | Pre-insulated | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE
PUB | Pipes / Drains | Thickness | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegmentDimension | Thickness | Length | mm | N.A | N.A
NEA | Pipes / Drains | Trade Effluent | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE
PUB | Pipes / Drains | Demountable Structure Above Pipe | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | RIGIDSEGMENT | SGPset_PipeSegment | DemountableStructureAbovePipe | Boolean | N.A | N.A | TRUE/FALSE
BCA | Pipes / Drains | Construction Method | Duct Fittings | Duct Fitting | N.A | Duct Accessory | MEP | IfcDuctFitting | Need not specify | SGPset_DuctFitting | ConstructionMethod | Label | N.A | N.A | N.A
BCA | Pipes / Drains | Pre-insulated | Duct Fittings | Duct Fitting | N.A | Duct Accessory | MEP | IfcDuctFitting | Need not specify | SGPset_DuctFitting | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE
BCA | Pipes / Drains | Construction Method | Ducts | Duct | N.A | Duct | MEP | IfcDuctSegment | Need not specify | SGPset_DuctSegment | ConstructionMethod | Label | N.A | N.A | N.A
BCA | Pipes / Drains | Pre-insulated | Ducts | Duct | N.A | Duct | MEP | IfcDuctSegment | Need not specify | SGPset_DuctSegment | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE
NEA | Pipes / Drains | Trade Effluent | Ducts | Duct | N.A | Duct | MEP | IfcDuctSegment | Need not specify | SGPset_DuctSegment | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE
NEA | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | *FLARESTACK | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | *RAINWATEROUTLET | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | *SCUPPERDRAIN | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipes | Pipe | N.A | Pipe | MEP | IfcPipeSegment | SPOOL | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *DRAINCHANNELBEND | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *FLANGEADAPTOR | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *FLEXIBLECOUPLING | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *PIPESILENCER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | *SHORTPIECE | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Pipes / Drains | Nominal Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | BEND | SGPset_PipeFittingDimension | NominalDiameter | Length | mm | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | ENTRY | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | EXIT | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | Material | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | JUNCTION | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | N.A | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | OBSTRUCTION | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Pipes / Drains | Inner Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFittingDimension | InnerDiameter | Length | mm | N.A | N.A
NEA | Pipes / Drains | Nominal Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFittingDimension | NominalDiameter | Length | mm | N.A | N.A
PUB | Pipes / Drains | Outer Diameter | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFittingDimension | OuterDiameter | Length | mm | N.A | N.A
PUB | Pipes / Drains | Thickness | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFittingDimension | Thickness | Length | mm | N.A | N.A
BCA | Pipes / Drains | Construction Method | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFitting | ConstructionMethod | Label | N.A | N.A | N.A
BCA | Pipes / Drains | Pre-insulated | Pipe Fittings | Pipe Fitting | N.A | Pipe Accessory | MEP | IfcPipeFitting | Need not specify | SGPset_PipeFitting | PreInsulated | Boolean | N.A | N.A | TRUE/FALSE
URA | Planter Box | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *PLANTERBOX | N.A | N.A | N.A | N.A | N.A | N.A
NParks | Planting Trough | N.A | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *LANDSCAPE_PLANTINGTROUGH | N.A | N.A | N.A | N.A | N.A | N.A
NPARKS | Planting Area | Approved Soil Mixture | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Area | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
NPARKS | Planting Area | Carpark Provision | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | CarparkProvision | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Compensated | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | Compensated | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Status | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | Status | Label | N.A | N.A | N.A
NPARKS | Planting Area | Turf | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | Turf | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Planting Area | Turf Species | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *PLANTINGAREA | SGPset_GeographicElement | TurfSpecies | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *AIRIMPURITIESSENSOR | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *FUELBURNINGEQUIPMENT | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *INCINERATOR | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ammonia And Ammonium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_AmmoniaAndAmmonium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Antimony | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Antimony | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Arsenic | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Benzene | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Benzene | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Cadmium | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Carbon Monoxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_CarbonMonoxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Chlorine | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Chlorine | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Copper | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Dioxins and Furans | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_DioxinsAndFurans | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Ethylene Oxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_EthyleneOxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Flourine And Hydrofluoric Acid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_FlourineAndHydrofluoricAcid | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Formaldehyde | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Formaldehyde | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenChloride | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Hydrogen Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_HydrogenSulphide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Lead | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_Mercury | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Oxides Of Nitrogen | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_OxidesOfNitrogen | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Particulate Substances | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_ParticulateSubstances | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Styrene Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_StyreneMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Dioxide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurDioxide | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide And Acid Gases | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideAndAcidGases | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Sulphur Trioxide Or Sulphuric Acid Mist | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_SulphurTrioxideOrSulphuricAcidMist | Label | N.A | N.A | N.A
NEA | Pollution Control | Air Impurities Vinyl Chloride Monomer | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | AI_VinylChlorideMonomer | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Arsenic | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Arsenic | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Barium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Barium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Beryllium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Beryllium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Biochemical Oxygen Demand | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_BiochemicalOxygenDemand | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Boron | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Boron | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Cadmium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Cadmium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Calcium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Calcium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Chemical Oxygen Demand | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_ChemicalOxygenDemand | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Chloride | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Chloride | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Chromium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Chromium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Colour | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Colour | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Copper | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Copper | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Cyanide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Cyanide | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Detergent | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Detergent | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Grease And Oil | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_GreaseAndOil | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Iron | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Iron | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Lead | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Lead | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Magnesium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Magnesium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Manganese | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Manganese | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Mercury | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Mercury | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Metals In Total | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_MetalsInTotal | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Nickel | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Nickel | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Nitrate | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Nitrate | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Phenolic Compound | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_PhenolicCompound | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Phosphate | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Phosphate | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge PH Value | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_PHValue | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Selenium | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Selenium | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Silver | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Silver | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Sulphate | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Sulphate | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Sulphide | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Sulphide | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Temperature Of Discharge | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_TemperatureOfDischarge | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Tin | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Tin | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Total Dissolved Solid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_TotalDissolvedSolid | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Total Suspended Solid | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_TotalSuspendedSolid | Label | N.A | N.A | N.A
NEA | Pollution Control | Trade Effluent Discharge Zinc | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *POLLUTIONCONTROLEQUIPMENT | SGPset_BuildingElementProxy | TED_Zinc | Label | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Rooms | Zone | N.A | Space | ARC | IfcSpace | *PRECASTEXTERNALWALLWITHCASTINWINDOWS | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Rooms | Zone | N.A | Space | ARC | IfcSpace | *PREFABRICATEDANDPREFINISHEDCEILING | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Rooms | Zone | N.A | Space | ARC | IfcSpace | *PREFABRICATEDANDPREFINISHEDFLOOR | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Rooms | Zone | N.A | Space | ARC | IfcSpace | *PREFABRICATEDANDPREFINISHEDWALL | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Rooms | Zone | N.A | Space | ARC | IfcSpace | *PREFABRICATEDBATHROOMUNIT | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | Mechanical Connection Type | Rooms | Zone | N.A | Space | ARC | IfcSpace | *PREFABRICATEDMEPHORIZONTALMODULE | SGPset_Space | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | Mechanical Connection Type | Rooms | Zone | N.A | Space | ARC | IfcSpace | *PREFABRICATEDMEPPLANTMODULE | SGPset_Space | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | Mechanical Connection Type | Rooms | Zone | N.A | Space | ARC | IfcSpace | *PREFABRICATEDMEPVERTICALMODULE | SGPset_Space | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | N.A | Rooms | Zone | N.A | Space | ARC | IfcSpace | *PREFABRICATEDPUMPSKID | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Prefabricated Building Systems and MEP Components | Is Common | Generic Models | Object | N.A | Object | MEP | IfcDiscreteAccessory | *PIPESUPPORT | SGPset_DiscreteAccessory | IsCommon | Boolean | N.A | N.A | TRUE/FALSE
BCA | System | Construction Method | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | CHILLEDWATER | SGPset_DistributionSystem | ConstructionMethod | Label | N.A | N.A | N.A
BCA | System | Pre-insulated | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | CHILLEDWATER | SGPset_DistributionSystem | PreInsulated | Label | N.A | N.A | N.A
BCA | Building | Project Development Type | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | ProjectDevelopmentType | Label | N.A | N.A | Residential (landed), Residential (non-landed), Mixed Development, Commercial, Industrial, Healthcare, Institutional, Agriculture, Transport Stations, Civil engineering works / Infrastructure, Free-standing structures, Others | Updated agency
BCA | Building | Owner Built Owner Stay | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcBuilding | Need not specify | SGPset_Building | OwnerBuiltOwnerStay | Boolean | N.A | N.A | TRUE/FALSE
PUB | Pump | Capacity | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | Capacity | VolumetricFlowRate | L/s or m3/s | N.A | N.A
PUB | Pump | Duty | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | Duty | Boolean | N.A | N.A | TRUE/FALSE
PUB | Pump | Pump Head | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | PumpHead | Label | m | N.A | 1m, 2m
PUB | Pump | Standby Pump | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | SUMPPUMP | SGPset_Pump | Standby | Boolean | N.A | N.A | TRUE/FALSE
PUB | Pump | N.A | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Pump | N.A | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Pump | N.A | Mechanical Equipment | Flow Equipment | N.A | Pump | MEP | IfcPump | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
URA | Racking System | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RACK | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Railing | Is Laminated | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_Railing | IsLaminated | Boolean | N.A | N.A | TRUE/FALSE
BCA | Railing | Safety Barrier | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_Railing | SafetyBarrier | Boolean | N.A | N.A | TRUE/FALSE
BCA | Railing | Type of Barrier | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_Railing | TypeOfBarrier | Label | N.A | N.A | N.A
BCA | Railing | Height | Railings | Railing | N.A | Railing | ARC | IfcRailing | GUARDRAIL | SGPset_RailingDimension | Height | Length | mm | N.A | N.A
BCA | Railing | Material | Railings | Railing | Component | Railing | STR | IfcRailing | GUARDRAIL | SGPset_Material | Material | Label | N.A | Name | N.A
BCA | Railing | N.A | Railings | Railing | Component | Railing | STR | IfcRailing | *BOLLARD | N.A | N.A | N.A | N.A | N.A | N.A
LTA | Ramp | Gradient | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_RampDimension | Gradient | Label | N.A | N.A | N.A
LTA | Ramp | Width | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_RampDimension | Width | Length | mm | N.A | N.A
LTA | Ramp | Transition Ramp | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_Ramp | TransitionRamp | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Vehicular | Ramps | Ramp | Item | Object | ARC | IfcRamp | *CURVEDRAMP | SGPset_Ramp | Vehicular | Boolean | N.A | N.A | TRUE/FALSE
BCA | Ramp | Barrier Free Accessibility | Ramps | Ramp | Item | Object | ARC | IfcRamp | *FLAREDKERBRAMP | SGPset_Ramp | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Accessway | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Accessway | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Egress | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Egress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Ingress | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Ingress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Ramp | Width | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_RampDimension | Width | Length | mm | N.A | N.A
LTA | Ramp | Material | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Material | Material | Label | N.A | N.A | TRUE/FALSE
LTA | Ramp | Vehicular | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | Vehicular | Boolean | N.A | N.A | TRUE/FALSE
BCA | Ramp | Barrier Free Accessibility | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_Ramp | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Ramp | Gradient | Ramps | Ramp | Item | Object | ARC | IfcRamp | STRAIGHT_RUN_RAMP | SGPset_RampDimension | Gradient | Label | N.A | N.A | N.A
BCA | Refuse Chute / Recyclables Chute | Chamfer Radius | Model Groups | IFC Assignments | N.A | System | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | ChamferRadius | Length | mm | N.A | N.A
BCA | Refuse Chute / Recyclables Chute | Construction Method | Model Groups | IFC Assignments | N.A | System | ARC | IfcSpace | Need not specify | SGPset_Space | ConstructionMethod | Label | N.A | N.A | Precast
BCA | Refuse Chute / Recyclables Chute | Inner Length | Model Groups | IFC Assignments | N.A | System | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | InnerLength | Length | mm | N.A | N.A
BCA | Refuse Chute / Recyclables Chute | Inner Width | Model Groups | IFC Assignments | N.A | System | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | InnerWidth | Length | mm | N.A | N.A
BCA | Refuse Chute / Recyclables Chute | Outer Length | Model Groups | IFC Assignments | N.A | System | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | OuterLength | Length | mm | N.A | N.A
BCA | Refuse Chute / Recyclables Chute | Outer Width | Model Groups | IFC Assignments | N.A | System | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | OuterWidth | Length | mm | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Construction Method | Walls | Wall | Panel | Wall | ARC | IfcWall | *REFUSECHUTE | SGPset_Wall | ConstructionMethod | Label | N.A | N.A | Precast
NEA | Refuse Chute / Recyclables Chute | N.A | Doors | Door | N.A | Door | ARC | IfcDoor | *ACCESSHATCH | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | N.A | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEACCESSPANEL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Air Tight | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | SGPset_Door | AirTight | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | Pset_DoorCommon | FireRating | Label | hr | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Self Closing | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | SGPset_Door | SelfClosing | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | Volume Controlled | Doors | Door | N.A | Door | ARC | IfcDoor | *RECYCLABLESCHUTEHOPPER | SGPset_Door | VolumeControlled | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | N.A | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEACCESSPANEL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Air Tight | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | SGPset_Door | AirTight | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | Fire Rating | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | Pset_DoorCommon | FireRating | Label | hr | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Self Closing | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | SGPset_Door | SelfClosing | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | Volume Controlled | Doors | Door | N.A | Door | ARC | IfcDoor | *REFUSECHUTEHOPPER | SGPset_Door | VolumeControlled | Boolean | N.A | N.A | TRUE/FALSE
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | Litre | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECOMPACTOR | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A
` | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | Litre | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *RECYCLABLECONTAINER | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | Litre | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECOMPACTOR | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Material | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | BasePlateMaterial | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Base Plate Thickness | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | BasePlateThickness | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Colour Code | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | ColourCode | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Compaction Ratio | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | CompactionRatio | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Hoop Up Point | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | HookUpPoint | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Litre | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | Litre | Label | N.A | N.A | N.A
NEA | Refuse Chute / Recyclables Chute | Tail Gate Orientation | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSECONTAINER | SGPset_Furniture | TailGateOrientation | Label | N.A | N.A | N.A
NEA | Refuse Handling Equipment | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *REFUSEBIN | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Refuse Handling Equipment | Compaction Ratio | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *REFUSEHANDLINGEQUIPMENT | SGPset_Tank | CompactionRatio | Label | N.A | N.A | N.A
NEA | Refuse Handling Equipment | Equipment Type | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *REFUSEHANDLINGEQUIPMENT | SGPset_Tank | EquipmentType | Label | N.A | N.A | N.A
NEA | Refuse Handling Equipment | Nominal Capacity | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *REFUSEHANDLINGEQUIPMENT | Pset_TankTypeCommon | NominalCapacity | Volume | L | N.A | N.A
SCDF | Road | Loading Capacity | Areas | Zone | N.A | Space | ARC | IfcBuildingElementProxy | *DRIVEWAY | SGPset_CivilElement | LoadingCapacity | Real | Tonnes | N.A | 24 tonnes
SCDF | Road | Designed Vehicle Mass | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_CivilElement | DesignedVehicleMass | Real | N.A | N.A | 30 tonnes
LTA | Road | Ingress | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_CivilElement | Egress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Road | Egress | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_CivilElement | Ingress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Road | Material | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPset_Material | Material | Label | N.A | Name | N.A
LTA | Road | Road Category | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *DRIVEWAY | SGPSet_CivilElement | RoadCategory | Label | N.A | Name | N.A
LTA | Road | Egress | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *CARRIAGEWAY | SGPset_CivilElement | Egress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Road | Ingress | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *CARRIAGEWAY | SGPset_CivilElement | Ingress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Road | Material | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *CARRIAGEWAY | SGPset_Material | Material | Label | N.A | Name | N.A
LTA | Road | Road Category | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *CARRIAGEWAY | SGPSet_CivilElement | RoadCategory | Label | N.A | Name | N.A
NEA | Road | Material | Areas | Zone | N.A | Space | ARC | IfcSpace | *ACCESSWAY | SGPset_Material | Material | Label | N.A | Name | N.A
| Road | Material | Areas | Zone | N.A | Space | ARC | IfcSpace | *PARKINGACCESSWAY | SGPset_Material | Material | Label | N.A | Name | N.A
SCDF | Road | Loading Capacity | Areas | Zone | N.A | Space | ARC | IfcSpace | *FIREENGINEACCESSROAD | SGPset_Space | LoadingCapacity | Real | tonnes | N.A | 30 tonnes
SCDF | Road | N.A | Areas | Zone | N.A | Space | ARC | IfcSpace | *FIREENGINEACCESSWAY | SGPset_Space | LoadingCapacity | Real | Tonnes | N.A | 24 tonnes
NEA | Road | Material | Areas | Zone | N.A | Space | ARC | IfcSpace | *VEHICULARSERVICEROAD | SGPset_Material | Material | Label | N.A | Name | N.A
LTA | Road | Width | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSPOINT | SGPset_BuildingElementProxyDimension | Width | Length | mm | N.A | N.A
LTA | Road | Egress | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSPOINT | SGPset_BuildingElementProxy | Egress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Road | Ingress | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSPOINT | SGPset_BuildingElementProxy | Ingress | Boolean | N.A | N.A | TRUE/FALSE
LTA | Road | Vehicular | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *ACCESSPOINT | SGPset_BuildingElementProxy | Vehicular | Boolean | N.A | N.A | TRUE/FALSE
LTA | Road | Height | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_CivilElementDimension | Height | Length | mm | N.A | N.A
LTA | Road | Thickness | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_CivilElementDimension | Thickness | Length | mm | N.A | N.A
LTA | Road | Kerb Type | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_CivilElement | KerbType | Label | N.A | N.A | N.A
LTA | Road | Material | Floors | Slab | Slab | Slab | ARC | IfcCivilElement | *ROADKERB | SGPset_Material | Material | Label | N.A | N.A | N.A
LTA | Road | N.A | Generic Models | Object | N.A | Object | ARC | IfcBuildingElementProxy | *HUMP | N.A | N.A | N.A | N.A | N.A | N.A
NParks | Roof | Construction Method | Roofs | Roof | N.A | Roof | ARC | IfcRoof | Need not specify | SGPset_Roof | ConstructionMethod | Label | N.A | N.A | N.A
NParks | Roof | Material | Roofs | Roof | N.A | Roof | ARC | IfcRoof | Need not specify | SGPset_Material | Material | Label | N.A | Name | N.A
URA | Roof | N.A | Roofs | Roof | N.A | Roof | ARC | IfcRoof | Need not specify | N.A | N.A | N.A | N.A | N.A | N.A
NParks | Roof | Construction Method | Roofs | Slab | Slab | Slab | ARC | IfcSlab | ROOF | SGPset_Slab | ConstructionMethod | Label | N.A | N.A | N.A
NParks | Roof | Material | Roofs | Slab | Slab | Slab | ARC | IfcSlab | ROOF | SGPset_Material | Material | Label | N.A | Name | N.A
NParks | Roof | Construction Method | Roofs | Roof | N.A | Roof | ARC | IfcCovering | ROOFING | SGPset_Covering | ConstructionMethod | Label | N.A | N.A | N.A
NParks | Roof | Material | Roofs | Roof | N.A | Roof | ARC | IfcCovering | ROOFING | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Sanitary Appliances (Bath) | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | BATH | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
PUB | Sanitary Appliances (Bidet) | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | BIDET | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
PUB | Sanitary Appliances (Shower) | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | SHOWER | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Sanitary Appliances (Urinal) | Ambulant Disabled | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | AmbulantDisabled | Boolean | N.A | N.A | TRUE/FALSE
BCA | Sanitary Appliances (Urinal) | Children Friendly | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE
BCA | Sanitary Appliances (Urinal) | Mounting | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | Mounting | Label | N.A | N.A | N.A
BCA | Sanitary Appliances (Urinal) | Waterless | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | Waterless | Boolean | N.A | N.A | TRUE/FALSE
PUB | Sanitary Appliances (Urinal) | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
NEA | Sanitary Appliances (Wash Basin) | Children Friendly | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | WASHHANDBASIN | SGPset_SanitaryTerminal | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE
NEA | Sanitary Appliances (Wash Basin) | Mounting | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | WASHHANDBASIN | SGPset_SanitaryTerminal | Mounting | Label | N.A | N.A | N.A
PUB | Sanitary Appliances (Wash Basin) | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | WASHHANDBASIN | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Sanitary Appliances (Water Closet) | Ambulant Disabled | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | AmbulantDisabled | Boolean | N.A | N.A | TRUE/FALSE
BCA | Sanitary Appliances (Water Closet) | Barrier Free Accessibility | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
NEA | Sanitary Appliances (Water Closet) | Children Friendly | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | ARC | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE
NEA | Sanitary Appliances (Water Closet) | Pan Mounting | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | PanMounting | Label | N.A | N.A | N.A
NEA | Sanitary Appliances (Water Closet) | Toilet Pan Type | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | *WATERCLOSET | SGPset_SanitaryTerminal | ToiletPanType | Label | N.A | N.A | N.A
PUB | Sanitary Appliances (Water Closet) | Water Efficiency Labelling Scheme (WELS) | Plumbing Fixtures | Pipe Flow Terminal | N.A | Fixture | MEP | IfcSanitaryTerminal | URINAL | SGPset_SanitaryTerminal | WELS | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Seating | Capacity | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | *BENCH | SGPset_Furniture | Capacity | Label | N.A | N.A | N.A
SCDF | Seating | N.A | Furniture | Object | N.A | Furniture | ARC | IfcFurniture | CHAIR | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Security Lighting | N.A | Lighting Fixtures | Object | N.A | Object | MEP | IfcLightFixture | SECURITYLIGHTING | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Sensor | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcSensor | LEVELSENSOR | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Shading Device | Shading Device | Generic Models | Object | N.A | Object | ARC | IfcShadingDevice | *LOUVREDPANEL | SGPset_ShadingDevice | ShadingDevice | Label | N.A | N.A | N.A
SCDF | Signage | Mounting Height | Specialty Equipment | Object | N.A | Object | ARC | IfcBuildingElementProxy | *SIGNAGE_EXIT | SGPset_BuildingElementProxy | MountingHeight | Length | mm | N.A | N.A
URA | Site | Number of Workers | Project Information | IFC Project Manager | N.A | Floor Manager | ARC | IfcSite | Need not specify | SGPset_Site | NumberOfWorkers | Integer | N.A | N.A | N.A
URA | Site | Total Area | Toposolid | Mesh | N.A | Mesh | ARC | IfcSite | Need not specify | Pset_SiteCommon | TotalArea | Area | m2 | N.A | N.A
NPARKS | Site Boundary | Approved Soil Mixture | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *CADASTRALLOT | SGPset_GeographicElement | ApprovedSoilMixture | Boolean | N.A | N.A | TRUE/FALSE
NPARKS | Site Boundary | Area | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *CADASTRALLOT | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
URA | Site Boundary | N.A | Toposolid | Mesh | N.A | Mesh | ARC | IfcGeographicElement | *CADASTRALLOT | N.A | N.A | N.A | N.A | N.A | N.A
URA | Site Boundary | N.A | Toposolid | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *CADASTRALLOT | N.A | N.A | N.A | N.A | N.A | N.A
URA | Site Boundary | N.A | Toposolid | Mesh | N.A | Mesh | External Works | IfcGeographicElement | *SITEBOUNDARY | SGPset_GeographicElementDimension | Area | Area | m2 | N.A | N.A
BCA | Slab | Accreditation PAS (Precaster Accreditation Scheme) | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Slab | Bottom Distribution Nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | BottomDistribution_nominal | Label | N.A | N.A | H25-150+H16-300
BCA | Slab | Bottom Main Nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | BottomMain_nominal | Label | N.A | N.A | H25-150+H16-300
BCA | Slab | Construction Method | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Slab | Lattice Girder Reinforcement | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | LatticeGirderReinforcement | Boolean | N.A | N.A | TRUE/FALSE
BCA | Slab | Load Bearing | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
BCA | Slab | Mark | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabDimension | Mark | Label | N.A | N.A | S1
BCA | Slab | Material Grade | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Slab | Mechanical Connection Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Slab | ReferTo2DDetail | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Slab | Reinforcement Steel Grade | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Slab | Shelter Usage | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | ShelterUsage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Slab | Slab Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | SlabType | Label | N.A | N.A | One way, Two way, Cantilever, Flat slab, Flat slab with drop panel, Transfer slab
BCA | Slab | Stirrups | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | Stirrups | Label | N.A | N.A | 1H10-150-300
BCA | Slab | Stirrups Type | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Slab | Thickness | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabDimension | Thickness | Length | mm | N.A | 300
BCA | Slab | Top Distribution nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | TopDistribution_nominal | Label | N.A | N.A | H25-150+H16-300
BCA | Slab | Top Main Nominal | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | TopMain_nominal | Label | N.A | N.A | H32-150+H20-300
BCA | Slab | Type Designator | Floors | Slab | Concrete Slab | Slab | STR | IfcSlab | Need not specify | SGPset_Slab | TypeDesignator | Label | N.A | N.A | N.A
BCA | Slab | Welded Mesh | Floors | Slab | Slab | Slab | STR | IfcSlab | Need not specify | SGPset_SlabReinforcement | WeldedMesh | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Soffit | Fire Rating | Roofs | Roof | N.A | Roof | ARC | IfcCovering | *SOFFIT | Pset_CoveringCommon | FireRating | Label | N.A | N.A | N.A
NEA | Sprinkler (Non-Fire; for NEA) | N.A | Sprinklers | Terminal | N.A | Sprinkler | MEP | IfcSanitaryTerminal | *SPRINKLER | N.A | N.A | N.A | N.A | N.A | N.A
URA | Space – Area Scheme | ACN_ActivityGeneratingUseType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_ActivityGeneratingUseType | Label | N.A | N.A | None, Double-sided, Single-sided
URA | Space – Area Scheme | ACN_CloseTime | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_CloseTime | Label | N.A | N.A | N.A
URA | Space – Area Scheme | ACN_ConnectivityType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_ConnectivityType | Label | N.A | N.A | Communal Sky Bridges (Within a Single Development, Covered Linkway, Covered Walkway, Elevated Pedestrian Link, Open Walkway, Public Space Node, Through Block Link, Underground Pedestrian Link
URA | Space – Area Scheme | ACN_IsOpen24HoursToPublic | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_IsOpen24HoursToPublic | Boolean | N.A | N.A | TRUE/FALSE
URA | Space – Area Scheme | ACN_IsPavingSpecified | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_IsPavingSpecified | Boolean | N.A | N.A | TRUE/FALSE
URA | Space – Area Scheme | ACN_OpenTime | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_OpenTime | Label | N.A | N.A | N.A
URA | Space – Area Scheme | ACN_PavingSpecification | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_CONNECTIVITY | SGPset_SpaceArea_Connectivity | ACN_PavingSpecification | Label | N.A | N.A | N.A
URA | Space – Area Scheme | AGF_BonusGFAType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_BonusGFAType | Label | N.A | N.A | Balcony Incentive Scheme, Conserved Bungalows Scheme, Indoor Recreation Spaces Scheme, Built Environment Transformation Scheme, Community and Sports Facilities Scheme, Rooftop ORA on Landscaped Roofs, ORA within Privately-Owned Public Spaces (POPS), CBD Incentive Scheme, Strategic Development Incentive (SDI) Scheme, Facade Articulation Scheme
URA | Space – Area Scheme | AGF_DevelopmentUse | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_DevelopmentUse | Label | N.A | N.A | N.A
URA | Space – Area Scheme | AGF_Name | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_Name | Label | N.A | N.A | Refer to Space Values sheet
URA | Space – Area Scheme | AGF_Note | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_Note | Label | N.A | N.A | N.A
URA | Space – Area Scheme | AGF_UnitNumber | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_UnitNumber | Label | N.A | N.A | N.A
URA | Space – Area Scheme | AGF_UseQuantum | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_GFA | SGPset_SpaceArea_GFA | AGF_UseQuantum | Label | N.A | N.A | Predominant, Ancillary
URA | Space – Area Scheme | ALS_GreeneryFeatures | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_LANDSCAPE | SGPset_SpaceArea_Landscape | ALS_GreeneryFeatures | Label | N.A | N.A | Communal Ground Garden, Extensive Green Roof, Green Buffer and Peripheral Planting Strip, Ground Landscaping, Landscape Deck - Vertical Greenery, Landscape Deck - Surface Greenery, Roof Top Landscaping, Sky Terrace, Urban Farm / Greenhouse, Vertical Greenery
URA | Space – Area Scheme | ALS_LandscapeType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_LANDSCAPE | SGPset_SpaceArea_Landscape | ALS_LandscapeType | Label | N.A | N.A | Decked/ Patterned Floor, Groundcovers, Landscaped Footpath, Shrubs, Turfing, Trees, Water Feature
URA | Space – Area Scheme | AST_AreaType | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_AreaType | Label | N.A | N.A | Accessory Lot, Common Property, Single User (Communal), Strata Lot (Private), Strata Lot (Communal)
URA | Space – Area Scheme | AST_Associated to | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_AssociatedTo | Label | N.A | N.A | N.A
URA | Space – Area Scheme | AST_Extg_StrataLotNumber | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_Extg_StrataLotNumber | Label | N.A | N.A | N.A
URA | Space – Area Scheme | AST_LegalArea | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_LegalArea | Integer | N.A | N.A | N.A
URA | Space – Area Scheme | AST_Prop_StrataLotNumber | Areas | Zone | N.A | Space | ARC | IfcSpace | *AREA_STRATA | SGPset_SpaceArea_Strata | AST_Prop_StrataLotNumber | Label | N.A | N.A | N.A
BCA | Space | Accreditation PAS (Precaster Accreditation Scheme) | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Ambulant Disabled | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | AmbulantDisabled | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
SCDF | Space | Area | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Area | Area | m2 | N.A | N.A
BCA | Space | Barrier Free Accessibility | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | BarrierFreeAccessibility | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Children Friendly | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | ChildrenFriendly | Boolean | N.A | N.A | TRUE/FALSE
PUB | Space | C Value | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | CValue | Label | N.A | N.A | 0.45 - 1
BCA | Space | Elderly Friendly | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | ElderlyFriendly | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Space | Emergency Voice Communication System | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | EmergencyVoiceCommunicationSystem | Label | N.A | N.A | 1-way EVC System, 2-way EVC System, Public Address System
SCDF | Space | Fire Detection And Suppression System | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FireDetectionAndSuppressionSystem | Label | N.A | N.A | Automatic Fire Alarm System, Automatic Sprinkler System, Water Mist System, Video Image Fire Detector System, Kitchen Hood Fire Extinguishing System, Clean Agent Fire Extinguishing System, Automatic Foam Sprinkler System, Foam Extinguisher System
SCDF | Space | Fire Emergency Ventilation Mode | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FireEmergencyVentilationMode | Label | N.A | N.A | Natural Ventilation, Mechanical Ventilation, Pressurisation, Cross-ventilation, Cross-ventilation with Intermediate Ventilation Opening, Vapour Extraction System (for spray painting room)
SCDF | Space | Fire Exit | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FireExit | Boolean | N.A | N.A | TRUE/FALSE
NParks | Space | Fully Covered With Tree Shrubs | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | FullyCoveredWithTreesShrubs | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Hearing Enhancement | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | HearingEnhancement | Boolean | N.A | N.A | TRUE/FALSE
BCA | Space | Height | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_SpaceDimension | Height | Length | mm | N.A | N.A
BCA | Space | Larger Accessible | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | LargerAccessible | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Space | Occupancy Load | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | OccupancyLoad | Real | N.A | N.A | N.A
URA | Space | Occupancy Type | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | OccupancyType | Label | N.A | N.A | Refer to Space Values sheet
LTA | Space | Parking Type | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | ParkingType | Label | N.A | N.A | Bicycle, Motorcycle
SCDF | Space | Purpose Group | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | PurposeGroup | Label | N.A | N.A | I, II, III
NEA | Space | Refuse Output | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | RefuseOutput | Real | N.A | N.A | 120, 200
BCA | Space | Retrofit | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | Retrofit | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Space | Smoke Control System | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SmokeControlSystem | Label | N.A | N.A | Smoke Vent, Smoke Purging System, Ductless Jet Fan System, Engineered Smoke Control System
NEA | Space | Sound Power Level | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SoundPowerLevel | Label | N.A | N.A | N.A
NEA | Space | Sound Pressure Level | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SoundPressureLevel | Label | N.A | N.A | N.A
BCA | Space | Space Name | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | SpaceName | Label | N.A | N.A | Refer to Space Values sheet
BCA | Space | Step Ramp Access | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | StepRampAccess | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Space | 24hr Manned Station | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | TwentyFourHourMannedStation | Boolean | N.A | N.A | TRUE/FALSE
URA | Space | Unit Number | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | UnitNumber | Label | N.A | N.A | N.A
BCA | Space | Ventilation Mode | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | VentilationMode | Label | N.A | N.A | Natural Ventilation, Air Conditioning, Mechanical Ventilation
SCDF | Space | Ventilation Type | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | VentilationType | Label | N.A | N.A | Cross Ventilation
BCA | Space | Volume | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | Volume | Volume | m3 | N.A | N.A
BCA | Staircase | Accreditation PAS (Precaster Accreditation Scheme) | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Staircase | Bottom Distribution | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | BottomDistribution | Label | N.A | N.A | H25-150+H16-300
BCA | Staircase | Bottom Main | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | BottomMain | Label | N.A | N.A | H25-150+H16-300
BCA | Staircase | Connection Details Bottom | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionDetailsBottom | Label | N.A | N.A | Detail 1
BCA | Staircase | Connection Details Top | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionDetailsTop | Label | N.A | N.A | Detail 1
BCA | Staircase | Connection Type Bottom | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionTypeBottom | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Staircase | Connection Type Top | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairSteelConnection | ConnectionTypeTop | Label | N.A | N.A | Pinned, Fixed, Free
BCA | Staircase | Construction Method | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
SCDF | Staircase | Fire Exit | Stairs | Stair | Component | Stair | ARC | IfcStair | Need not specify | Pset_StairCommon | FireExit | Boolean | N.A | N.A | TRUE/FALSE
BCA | Staircase | Mark | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | Mark | Label | N.A | N.A | ST1, ST-A1
BCA | Staircase | Material Grade | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Staircase | Mechanical Connection Type | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Staircase | Member Section | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairDimension | MemberSection | Label | N.A | N.A | RHS600x30x4, CHS500x3.0, 254x254x63 kg/m
BCA | Staircase | ReferTo2DDetail | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Staircase | Reinforcement Steel Grade | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Staircase | Section Fabrication Method | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_Stair | SectionFabricationMethod | Label | N.A | N.A | Hot rolled, Cold formed
BCA | Staircase | Thickness | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairDimension | Thickness | Length | mm | N.A | 150
BCA | Staircase | Top Distribution | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | TopDistribution | Label | N.A | N.A | H25-150+H16-300
BCA | Staircase | Top Main | Stairs | Stair | Component | Stair | STR | IfcStair | Need not specify | SGPset_StairReinforcement | TopMain | Label | N.A | N.A | H32-150+H20-300
BCA | Staircase | Width | Stairs | Stair | Component | Stair | ARC | IfcStair | Need not specify | SGPset_StairDimension | Width | Length | mm | N.A | 2200
SCDF | Staircase | Width | Stairs | Stair | Component | Stair | ARC | IfcStair | Need not specify | SGPset_StairDimension | Width | Length | mm | N.A | 2200
BCA | Staircase | Riser Count | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | NumberOfRisers | Integer | N.A | N.A | N.A
BCA | Staircase | Riser Height | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | RiserHeight | Length | mm | N.A | N.A
SCDF | Staircase | Riser Height | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | RiserHeight | Length | mm | N.A | N.A
SCDF | Staircase | Tread Length | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | TreadLength | Length | mm | N.A | N.A
BCA | Staircase | Tread Width | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | TreadLength | Length | mm | N.A | N.A
BCA | Staircase | Tread Count | Stairs | Stair | Component | Stair | ARC | IfcStairFlight | Need not specify | Pset_StairFlightCommon | NumberOfTreads | Integer | N.A | N.A | N.A
BCA | Staircase | Construction Method | Stairs | Stair | Component | Stair | STR | IfcStairFlight | Need not specify | SGPset_StairFlight | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Staircase | Material Grade | Stairs | Stair | Component | Stair | STR | IfcStairFlight | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Staircase | Mechanical Connection Type | Stairs | Stair | Component | Stair | STR | IfcStairFlight | Need not specify | SGPset_StairFlight | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | CHILLEDWATER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DOMESTICCOLDWATER | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
PUB | System | Length | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DOMESTICCOLDWATER | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A
PUB | System | Material | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DOMESTICCOLDWATER | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | DRAINAGE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *DRYRISER | N.A | N.A | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *FOAMFIREEXTINGUISHING | N.A | N.A | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *FOAMSPRINKLER | N.A | N.A | N.A | N.A | N.A
PUB | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
PUB | System | Length | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A
PUB | System | Material | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *POTABLEWATER | SGPset_Material | Material | Label | N.A | Name | N.A
NEA | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | RAINWATER | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
NEA | System | Gradient | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | RAINWATER | SGPset_PipeSegmentDimension | Gradient | Label | N.A | N.A | N.A
PUB | System | N.A | Piping Systems | MEP System | N.A | System | External Works | IfcDistributionSystem | RAINWATER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | System | Diameter | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | SGPset_PipeSegmentDimension | Diameter | Length | mm | N.A | N.A
PUB | System | Gradient | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | SGPset_PipeSegmentDimension | Gradient | Label | N.A | N.A | N.A
PUB | System | Length | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SANITARY | SGPset_PipeSegmentDimension | Length | Length | mm | N.A | N.A
NEA | System | Trade Effluent | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | SEWAGE | SGPset_PipeSegment | TradeEffluent | N.A | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *SPRINKLER | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | System | N.A | Piping Systems | MEP System | N.A | System | MEP | IfcDistributionSystem | *WETRISER | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | Diameter | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Diameter | Length | mm | N.A | N.A
PUB | Tank | Height | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Height | Length | mm | N.A | N.A
PUB | Tank | Length | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Length | Length | mm | N.A | N.A
PUB | Tank | Width | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_TankDimension | Width | Length | mm | N.A | N.A
PUB | Tank | Nominal Capacity | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | Pset_TankTypeCommon | NominalCapacity | Volume | L | N.A | N.A
PUB | Tank | Is Potable | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | SGPset_Tank | IsPotable | Boolean | N.A | N.A | TRUE/FALSE
SCDF | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | STORAGE | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | Height | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_TankDimension | Height | Length | mm | N.A | N.A
PUB | Tank | Length | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_TankDimension | Length | Length | mm | N.A | N.A
PUB | Tank | Width | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_TankDimension | Width | Length | mm | N.A | N.A
PUB | Tank | Nominal Capacity | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | Pset_TankTypeCommon | NominalCapacity | Volume | L | N.A | N.A
PUB | Tank | Is Potable | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *DETENTIONTANK | SGPset_Tank | IsPotable | Boolean | N.A | N.A | TRUE/FALSE
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *RAINWATERHARVESTINGTANK | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *IRRIGATIONTANK | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *SPRINKLERTANK | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | Trade Effluent | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *BALANCINGTANK | SGPset_Tank | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *SECTIONAL | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | VESSEL | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank | N.A | Mechanical Equipment | Object | N.A | Object | MEP | IfcTank | *RECHARGEWELL | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Tank (RC Tank) | Is Potable | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | IsPotable | Boolean | N.A | N.A | TRUE/FALSE
PUB | Tank (RC Tank) | NominalCapacity | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | NominalCapacity | Real | N.A | N.A | N.A
PUB | Tank (RC Tank) | Thickness | Rooms | Zone | N.A | Space | ARC | IfcSpace | Need not specify | SGPset_Space | Thickness | Length | N.A | N.A | N.A
PUB | Type Bedding for Pipe | BeddingType | Generic Models | Object | N.A | Object | External Works | IfcPipeSegment | *FOUNDATION | SGPset_PipeSegment | BeddingType | Label | N.A | N.A | Type 1, Type 2, Type 3
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *AIRADMITTANCE | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *DRAINOFFCOCK | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *LANDINGVALVE | N.A | N.A | N.A | N.A | N.A | N.A
SCDF | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | *SPRINKLERCONTROL | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | CHECK | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | DOUBLECHECK | N.A | N.A | N.A | N.A | N.A | N.A
NEA | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | ISOLATING | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Valve | N.A | Pipe Accessories | Pipe In-line Flow Device | N.A | Valve | MEP | IfcValve | MIXING | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Wall | Accreditation PAS (Precaster Accreditation Scheme) | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | Accreditation_PAS | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Arrangement Type | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ArrangementType | Label | N.A | N.A | N.A
BCA | Wall | Beam Façade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | BeamFacade | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Construction Method | Walls | Wall | Panel | Wall | ARC | IfcWall | Need not specify | SGPset_Wall | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Wall | Construction Method | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ConstructionMethod | Label | N.A | N.A | CIS, PC, PT (Pre), PT (Post), PF, PPVC
BCA | Wall | Double Bay Façade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | Double Bay Façade | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Horizontal Rebar | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | HorizontalRebar | Label | N.A | N.A | H20-150
BCA | Wall | Is External | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | IsExternal | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Is Party Wall | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | IsPartyWall | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Load Bearing | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | LoadBearing | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Mark | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallDimension | Mark | Label | N.A | N.A | W1
BCA | Wall | Material Grade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Material | MaterialGrade | Label | N.A | Name | C12/15, C20/25, C30/37, C35/45, C40/50, C50/60, C55/67, C60/75, C70/85, C80/95, S235, S275, S355, S460, High Strength Concrete
BCA | Wall | Mechanical Connection Type | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | MechanicalConnectionType | Label | N.A | N.A | N.A
BCA | Wall | Prefabricated Reinforcement Cage | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | PrefabricationReinforcementCage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Prefinished Façade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | Prefinished Façade | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | ReferTo2DDetail | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ReferTo2DDetail | Label | N.A | N.A | Dwg Number
BCA | Wall | Reinforcement Steel Grade | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ReinforcementSteelGrade | Label | N.A | N.A | 500A, 500B, 500C, 600A, 600B, 600C
BCA | Wall | Shelter Usage | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_Wall | ShelterUsage | Boolean | N.A | N.A | TRUE/FALSE
BCA | Wall | Stirrups | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | Stirrups | Label | N.A | N.A | H10-150-300
BCA | Wall | Stirrups Type | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | StirrupsType | Label | N.A | N.A | Normal, U, C, CL [for civil defence shelter], Torsion
BCA | Wall | Thickness | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallDimension | Thickness | Length | mm | N.A | 300
BCA | Wall | Vertical Rebar | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallReinforcement | VerticalRebar | Label | N.A | N.A | H32-150+H25-150
BCA | Wall | Working Load DA1-1 | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallStructuralLoad | WorkingLoad_DA1-1 | Integer | kN | N.A | 1234
BCA | Wall | Working Load DA1-2 | Walls | Wall | Concrete Panel | Wall | STR | IfcWall | Need not specify | SGPset_WallStructuralLoad | WorkingLoad_DA1-2 | Integer | kN | N.A | 1234
URA | Wall | N.A | Walls | Wall | Panel | Wall | ARC | IfcWall | PARAPET | N.A | N.A | N.A | N.A | N.A | N.A
URA | Wall | N.A | Walls | Wall | Panel | Wall | ARC | IfcWall | RETAININGWALL | N.A | N.A | N.A | N.A | N.A | N.A
NParks | Wall | N.A | Walls | Wall | Panel | Wall | ARC | IfcWall | *BOUNDARYWALL | N.A | N.A | N.A | N.A | N.A | N.A
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | FLOORTRAP | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | FLOORWASTE | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | GULLYSUMP | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | GULLYTRAP | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | WASTETRAP | SGPset_Material | Material | Label | N.A | Name | N.A
PUB | Waste Terminal | Material | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | *WASTESUMP | SGPset_Material | Material | Label | N.A | Name | N.A
NEA | Waste Terminal | Trade Effluent | Pipe Accessories | Pipe Flow Terminal | N.A | Fixture | MEP | IfcWasteTerminal | *WASTESUMP | SGPset_WasteTerminal | TradeEffluent | Boolean | N.A | N.A | TRUE/FALSE
PUB | Water Meter | Capacity | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | SGPset_FlowMeter | Capacity | Volume | L/s | N.A | N.A
PUB | Water Meter | Diameter | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | SGPset_FlowMeterDimension | Diameter | Length | mm | N.A | N.A
PUB | Water Meter | Length | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | SGPset_FlowMeterDimension | Length | Length | mm | N.A | N.A
PUB | Water Meter | Purpose | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | Purpose | Label | N.A | N.A | PRIVATE
PUB | Water Meter | Unit Number | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | UnitNumber | Label | N.A | N.A | N.A
PUB | Water Meter | Unit Number Tag | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | UnitNumberTag | Boolean | N.A | N.A | TRUE/FALSE
PUB | Water Meter | Water Supply Source | Pipe Accessories | Pipe In-line Flow Device | N.A | Pipe Accessory | MEP | IfcFlowMeter | WATERMETER | Pset_FlowMeterOccurrence | WaterSupplySource | Label | N.A | N.A | N.A
URA | Window | Operation Type | Windows | Window | N.A | Window | ARC | IfcWindow | *BAYWINDOW | SGPset_Window | OperationType | Label | N.A | N.A | N.A
BCA | Window | Inner Diameter | Windows | Window | N.A | Window | ARC | IfcWindow | *VENTILATIONSLEEVE | SGPset_WindowDimension | InnerDiameter | Length | mm | N.A | N.A
BCA | Window | Outer Diameter | Windows | Window | N.A | Window | ARC | IfcWindow | *VENTILATIONSLEEVE | SGPset_WindowDimension | OuterDiameter | Length | mm | N.A | N.A
URA | Window | Material | Windows | Window | N.A | Window | ARC | IfcWindow | Need not specify | SGPset_Material | Material | Label | N.A | Name | N.A
SCDF | Window | Safety Barrier Height | Windows | Window | N.A | Window | ARC | IfcWindow | Need not specify | SGPset_Window | SafetyBarrierHeight | Real | N.A | N.A | N.A
SCDF | Window | Fire Access Opening | Windows | Window | N.A | Window | ARC | IfcWindow | WINDOW | SGPset_Window | FireAccessOpening | Boolean | N.A | N.A | TRUE/FALSE
BCA | Window | Structural Height | Windows | Window | N.A | Window | ARC | IfcWindow | WINDOW | SGPset_WindowDimension | StructuralHeight | Length | mm | N.A | N.A
BCA | Window | Structural Width | Windows | Window | N.A | Window | ARC | IfcWindow | WINDOW | SGPset_WindowDimension | StructuralWidth | Length | mm | N.A | N.A
BCA | Window | Percentage of Opening | Windows | Window | N.A | Window | ARC | IfcWindow | WINDOW | SGPset_Window | PercentageOfOpening | Real | N.A | N.A | N.A
BCA | Window | N.A | Windows | Window | N.A | Window | ARC | IfcWindow | SKYLIGHT | N.A | N.A | N.A | N.A | N.A | N.A
BCA | Window | N.A | Windows | Window | N.A | Window | ARC | IfcWindow | LOUVRE | N.A | N.A | N.A | N.A | N.A | N.A

## Space Values
Property | Property Value
OccupancyType | single dwelling residential
OccupancyType | multi-unit residential
OccupancyType | supervisory care facility
OccupancyType | supervisory care facility (detention)
OccupancyType | nursing care facilities
OccupancyType | hospital without A&E services
OccupancyType | hospital with A&E services
OccupancyType | ambulatory care facility
OccupancyType | ambulatory care facility (standalone)
OccupancyType | custodian care facility
OccupancyType | custodian care facility (nursery)
OccupancyType | public education institution
OccupancyType | private education institution
OccupancyType | workers dormitory
OccupancyType | office
OccupancyType | telephone exchange/ central office
OccupancyType | factory office
OccupancyType | shop
OccupancyType | ODA
OccupancyType | outpatient clinic
OccupancyType | polyclinic
OccupancyType | market
OccupancyType | temporary showflat
OccupancyType | factory showroom
OccupancyType | petrol station
OccupancyType | factory
OccupancyType | food production factory
OccupancyType | M&E area
OccupancyType | wafer fabrication plant
OccupancyType | trade effluent treatment plant
OccupancyType | waste management and recycling
OccupancyType | embalming facility
OccupancyType | agriculture
OccupancyType | animal related facility
OccupancyType | high containment facility
OccupancyType | electrical & gas facility
OccupancyType | road tunnel
OccupancyType | body treatment place
OccupancyType | entertainment place
OccupancyType | assembly place
OccupancyType | cinema
OccupancyType | recreational place
OccupancyType | sky terrace
OccupancyType | F&B outlet
OccupancyType | fast food outlet
OccupancyType | ORA
OccupancyType | food centre
OccupancyType | educational place
OccupancyType | serviced apartment
OccupancyType | hostel
OccupancyType | hotel
OccupancyType | backpacker hotel
OccupancyType | capsule hotel
OccupancyType | community club
OccupancyType | social club
OccupancyType | religious place
OccupancyType | park
OccupancyType | sports facility
OccupancyType | sports facility (ancillary)
OccupancyType | residential amenities
OccupancyType | train station
OccupancyType | air transport terminal
OccupancyType | sea transport terminal
OccupancyType | land transport terminal
OccupancyType | rail depot
OccupancyType | bus depot
OccupancyType | Parking
OccupancyType | FAMCP
OccupancyType | warehouse
OccupancyType | chemical/ hazmat storage
OccupancyType | storage
OccupancyType | airbase
OccupancyType | live firing area
OccupancyType | training area
OccupancyType | campsite
OccupancyType | wet play field
OccupancyType | reservoir
OccupancyType | river
OccupancyType | canal
OccupancyType | major drain
OccupancyType | pond
OccupancyType | lake
OccupancyType | other waterbody
OccupancyType | nature reserve
OccupancyType | nature area
OccupancyType | school field
OccupancyType | promenade
OccupancyType | marina
OccupancyType | quarry
SpaceName | balcony
SpaceName | bedroom
SpaceName | master bedroom
SpaceName | maid room
SpaceName | guestroom
SpaceName | bathroom
SpaceName | master bath
SpaceName | maid bath
SpaceName | yard bath
SpaceName | dining room
SpaceName | dining area
SpaceName | household shelter
SpaceName | kitchen
SpaceName | living room
SpaceName | living area
SpaceName | loft
SpaceName | private lift lobby
SpaceName | private enclosed space
SpaceName | service yard
SpaceName | study
SpaceName | toilet
SpaceName | walkin wardrobe
SpaceName | staff quarters
SpaceName | student bedroom individual
SpaceName | student bedroom multipax
SpaceName | housekeeping
SpaceName | isolation ward toilet
SpaceName | accessible washroom
SpaceName | male toilet
SpaceName | female toilet
SpaceName | unisex toilet
SpaceName | family-friendly washroom
SpaceName | washroom with shower
SpaceName | powder room
SpaceName | changing room
SpaceName | female changing room
SpaceName | male changing room
SpaceName | locker room
SpaceName | restroom
SpaceName | lactation room
SpaceName | sick room
SpaceName | shower room
SpaceName | shower stall
SpaceName | wash area
SpaceName | archive room (reading)
SpaceName | archive room (stack)
SpaceName | ball room
SpaceName | banking hall
SpaceName | bazaar
SpaceName | business centre
SpaceName | business office
SpaceName | classroom
SpaceName | clean room
SpaceName | computer classroom
SpaceName | common room
SpaceName | computer room
SpaceName | concierge
SpaceName | conference room
SpaceName | consultant room
SpaceName | crematoria
SpaceName | dance studio
SpaceName | department store
SpaceName | design studio
SpaceName | detention room
SpaceName | exposition
SpaceName | trade fair area
SpaceName | filing room
SpaceName | store
SpaceName | fire command centre
SpaceName | function room
SpaceName | exhibits gallery
SpaceName | choir gallery
SpaceName | prayer gallery
SpaceName | seating gallery
SpaceName | trading gallery
SpaceName | viewing gallery
SpaceName | guard house
SpaceName | hobby room
SpaceName | kiosk
SpaceName | laboratory
SpaceName | laundry
SpaceName | library room (stack)
SpaceName | library room (reading)
SpaceName | lounge
SpaceName | machine/printing room
SpaceName | mailroom
SpaceName | meeting room
SpaceName | music studio
SpaceName | night club
SpaceName | admin office
SpaceName | general office
SpaceName | ancillary office
SpaceName | director office
SpaceName | manager office
SpaceName | drafting office
SpaceName | outdoor display area
SpaceName | packing area
SpaceName | distribution area
SpaceName | pantry
SpaceName | prayer hall
SpaceName | prayer room
SpaceName | male prayer room
SpaceName | female prayer room
SpaceName | pre-function room
SpaceName | production area
SpaceName | promotion area
SpaceName | reading room
SpaceName | reception area
SpaceName | seminar room
SpaceName | security room
SpaceName | service area
SpaceName | shed
SpaceName | shop
SpaceName | showflat
SpaceName | showroom
SpaceName | society room
SpaceName | spray painting room
SpaceName | staff office
SpaceName | staff lounge
SpaceName | supermarket
SpaceName | therapy centre
SpaceName | ticketing office
SpaceName | trading floor
SpaceName | visitors lounge
SpaceName | waiting area
SpaceName | workshop
SpaceName | bar
SpaceName | pub
SpaceName | café
SpaceName | cafeteria
SpaceName | canteen
SpaceName | food stall
SpaceName | service counter
SpaceName | restaurant
SpaceName | snack bar
SpaceName | staff canteen
SpaceName | area of refuge
SpaceName | clinic
SpaceName | consultation room
SpaceName | examination room
SpaceName | surgical viewing gallery
SpaceName | nursing room
SpaceName | nursing station
SpaceName | operation theatre
SpaceName | outpatient waiting area
SpaceName | patient accommodation intensive care
SpaceName | patient accommodation ward
SpaceName | isolation ward
SpaceName | pharmacy staff area
SpaceName | pharmacy waiting area
SpaceName | treatment room
SpaceName | amphitheatre
SpaceName | amphitheatre without fixed seating
SpaceName | auditorium
SpaceName | auditorium without fixed seating
SpaceName | cinema
SpaceName | cinema without fixed seating
SpaceName | grandstand
SpaceName | grandstand without fixed seating
SpaceName | assembly hall
SpaceName | assembly hall without fixed seating
SpaceName | concert hall
SpaceName | concert hall without fixed seating
SpaceName | exhibition hall
SpaceName | exhibition hall without fixed seating
SpaceName | conference hall
SpaceName | conference hall without fixed seating
SpaceName | function hall
SpaceName | function hall without fixed seating
SpaceName | lecture room
SpaceName | lecture room without fixed seating
SpaceName | spectator area
SpaceName | spectator area without fixed seating
SpaceName | theatre
SpaceName | theatre without fixed seating
SpaceName | indoor sport hall
SpaceName | multi-purpose hall
SpaceName | multi-purpose room
SpaceName | multi-purpose sports hall
SpaceName | audio visual area
SpaceName | audio visual control room
SpaceName | audio visual lighting control room
SpaceName | live entertainment
SpaceName | live performance
SpaceName | orchestral pit
SpaceName | projection room
SpaceName | back stage
SpaceName | front stage
SpaceName | amusement park
SpaceName | billiards room
SpaceName | body massage
SpaceName | bowling alley
SpaceName | bowling lane
SpaceName | casino
SpaceName | children playground
SpaceName | club room
SpaceName | discotheque dancing area
SpaceName | discotheque dining area
SpaceName | hockey field
SpaceName | hockey pitch
SpaceName | rugby field
SpaceName | rugby pitch
SpaceName | soccer field
SpaceName | soccer pitch
SpaceName | fitness corner
SpaceName | foot reflexology
SpaceName | fitness club
SpaceName | fitness centre
SpaceName | gaming centre
SpaceName | gymnasium
SpaceName | health club
SpaceName | health centre
SpaceName | indoor games room
SpaceName | karaoke lounge
SpaceName | karaoke dining area
SpaceName | recreation room
SpaceName | refreshmen area
SpaceName | skating rink
SpaceName | spa
SpaceName | badminton court
SpaceName | basketball court
SpaceName | basketball half court
SpaceName | futsal court
SpaceName | netball court
SpaceName | netball half court
SpaceName | squash court
SpaceName | tennis court
SpaceName | tennis half court
SpaceName | volleyball court
SpaceName | swimming pool
SpaceName | swimming pool deck
SpaceName | training area
SpaceName | backyard
SpaceName | courtyard
SpaceName | construction site
SpaceName | outdoor refreshment area
SpaceName | pavilion
SpaceName | roof
SpaceName | green roof
SpaceName | private roof garden
SpaceName | jogging track
SpaceName | footpath
SpaceName | sunken planting area
SpaceName | garden
SpaceName | battery room
SpaceName | cooling tower
SpaceName | equipment disinfection room
SpaceName | equipment washing bay
SpaceName | lubrication bay
SpaceName | pulley room
SpaceName | mechnical plant room
SpaceName | ac plant room
SpaceName | ahu room
SpaceName | boiler room
SpaceName | boiler room (oil fired)
SpaceName | chiller room
SpaceName | discharge valve chamber
SpaceName | electric lift motor room
SpaceName | electrical room
SpaceName | essential fan room
SpaceName | fire pump room
SpaceName | balancing pump room
SpaceName | domestic pump room
SpaceName | irrigation pump room
SpaceName | portable water pump room
SpaceName | sprinkler pump room
SpaceName | pumped sanitary system room
SpaceName | pumped drainage system room
SpaceName | ejector room
SpaceName | emergency generator room
SpaceName | generator room
SpaceName | high voltage switch room
SpaceName | hydraulic lift motor room
SpaceName | lift machine room
SpaceName | lift motor room
SpaceName | low voltage switch room
SpaceName | oil tank room
SpaceName | sprinkler tank room
SpaceName | telecommunication room
SpaceName | equipment room
SpaceName | transformer room
SpaceName | wet riser tank room
SpaceName | electrical switchgear room
SpaceName | PABX room
SpaceName | server room
SpaceName | mdf room
SpaceName | mobile installation space
SpaceName | mobile deployment space
SpaceName | electronics parking system room
SpaceName | police equipment room
SpaceName | vent room
SpaceName | substation
SpaceName | meter compartment
SpaceName | domestic transfer tank room
SpaceName | hosereel tank room
SpaceName | hydrant tank room
SpaceName | NEWater tank room
SpaceName | non-potable water tank room
SpaceName | potable water tank room
SpaceName | balancing tank
SpaceName | detention tank
SpaceName | domestic booster tank
SpaceName | domestic water tank
SpaceName | hot water tank
SpaceName | make up water tank
SpaceName | NEWater tank
SpaceName | pneumatic tank
SpaceName | portable water tank
SpaceName | rainwater harvesting tank
SpaceName | irrigation tank
SpaceName | sprinkler tank
SpaceName | refuse chute chamber
SpaceName | refuse room
SpaceName | bin center
SpaceName | bin point
SpaceName | coldroom
SpaceName | deposit room
SpaceName | strong room
SpaceName | mortuary
SpaceName | storage
SpaceName | storeroom
SpaceName | warehouse
SpaceName | industrial waste storage area
SpaceName | driveway
SpaceName | garage
SpaceName | parking place
SpaceName | vehicle washing bay
SpaceName | loading/unloading bay
SpaceName | loading/unloading platform
SpaceName | alighting point
SpaceName | boarding point
SpaceName | drop off point
SpaceName | bus stop
SpaceName | taxi bay
SpaceName | taxi shelter
SpaceName | atrium
SpaceName | concourse
SpaceName | foyer
SpaceName | passenger arrival area
SpaceName | passenger departure area
SpaceName | cargo lift lobby
SpaceName | goods lift lobby
SpaceName | common lobby
SpaceName | evacuation lift lobby
SpaceName | fire lift lobby
SpaceName | passenger lift lobby
SpaceName | protected lobby
SpaceName | smoke-free lobby
SpaceName | service lift lobby
SpaceName | equipment platform
SpaceName | pedestrian linkway (with commercial activities)
SpaceName | pedestrian linkway (building to Rapid Transit Stations without commercial activities)
SpaceName | pedestrian linkway (building to building without commercial activities)
SpaceName | pedestrian linkway (standalone type without commercial activities)
SpaceName | promenade
SpaceName | boardwalk
SpaceName | through-block link
SpaceName | access aisle
SpaceName | private corridor
SpaceName | corridor
SpaceName | external corridor
SpaceName | open walkway
SpaceName | covered walkway
SpaceName | footway
SpaceName | pathway
SpaceName | veranda
SpaceName | void deck
SpaceName | external exit staircase
SpaceName | internal exit staircase
SpaceName | external exit passageway
SpaceName | internal exit passageway
SpaceName | external exit ramp
SpaceName | internal exit ramp
SpaceName | staircase
SpaceName | airlock
SpaceName | letter box
SpaceName | dry riser shaft
SpaceName | electrical shaft
SpaceName | gas shaft
SpaceName | ventilation shaft
SpaceName | water shaft
SpaceName | wet riser shaft
SpaceName | lift shaft
SpaceName | telecommunication shaft
SpaceName | chilled water shaft
SpaceName | sewerage shaft
SpaceName | exhaust shaft
SpaceName | refuse chute
SpaceName | recyclables chute
SpaceName | household non-shelter
SpaceName | storey shelter
SpaceName | storey non-shelter
SpaceName | staircase storey shelter
SpaceName | staircase storey non-shelter
SpaceName | rest area
SpaceName | airwell
AGF_DevelopmentUse | Agriculture
AGF_DevelopmentUse | Beach Area
AGF_DevelopmentUse | Business Park
AGF_DevelopmentUse | Business 1
AGF_DevelopmentUse | Business 2
AGF_DevelopmentUse | Cemetery
AGF_DevelopmentUse | Civic & Community Institution
AGF_DevelopmentUse | Community Institution
AGF_DevelopmentUse | Commercial
AGF_DevelopmentUse | Educational Institution
AGF_DevelopmentUse | Health & Medical Care
AGF_DevelopmentUse | Hotel
AGF_DevelopmentUse | Open Space
AGF_DevelopmentUse | Park
AGF_DevelopmentUse | Place of Worship
AGF_DevelopmentUse | Port/Airport
AGF_DevelopmentUse | Rapid Transit
AGF_DevelopmentUse | Reserve Site
AGF_DevelopmentUse | Residential (Landed)
AGF_DevelopmentUse | Residential (Non-landed)
AGF_DevelopmentUse | Road
AGF_DevelopmentUse | Special Use
AGF_DevelopmentUse | Sports & Recreation
AGF_DevelopmentUse | Transport Facilities
AGF_Name | AC Ledge
AGF_Name | Airwell
AGF_Name | ATM Kiosk
AGF_Name | Balcony
AGF_Name | Bicycle Parking Space
AGF_Name | Cable Chamber
AGF_Name | Car Parking Lot (Mechanised)
AGF_Name | Car Porch/ Garage
AGF_Name | Conserved Bungalow
AGF_Name | Courtyard
AGF_Name | Covered Walkway/ Linkages
AGF_Name | Driveways
AGF_Name | End of Trip Facilities
AGF_Name | Entrance Canopy
AGF_Name | Guardhouse / Sentry Post
AGF_Name | Household Shelter
AGF_Name | Indoor Recreation Space
AGF_Name | Letter Box Area
AGF_Name | Lift Area
AGF_Name | Lift Motor Room
AGF_Name | Loading and Unloading Bay
AGF_Name | M&E Floor
AGF_Name | M&E Room (enclosed)
AGF_Name | M&E Services (non-load bearing covering above)
AGF_Name | M&E Space (unenclosed)
AGF_Name | Meter Compartment
AGF_Name | Outdoor Refreshment Area
AGF_Name | Outdoor Refreshment Kiosk
AGF_Name | Pavilion
AGF_Name | Pick-up/ Drop-off Point
AGF_Name | Private Enclosed Space
AGF_Name | Privately Owned Public Space
AGF_Name | RC Ledge
AGF_Name | Refuse Chamber
AGF_Name | Residual Area (Carpark Floor)
AGF_Name | Roof Terrace/ Garden
AGF_Name | Stage
AGF_Name | Swimming Pool
AGF_Name | Façade Articulation
AGF_Name | Vending Machine Kiosk
AGF_Name | Others
AGF_BonusGFAType | Balcony Incentive Scheme
AGF_BonusGFAType | Conserved Bungalows Scheme
AGF_BonusGFAType | Indoor Recreation Spaces Scheme
AGF_BonusGFAType | Built Environment Transformation Scheme
AGF_BonusGFAType | Community and Sports Facilities Scheme
AGF_BonusGFAType | Rooftop ORA on Landscaped Roofs
AGF_BonusGFAType | ORA within Privately-Owned Public Spaces (POPS)
AGF_BonusGFAType | CBD Incentive Scheme
AGF_BonusGFAType | Strategic Development Incentive (SDI) Scheme
AGF_BonusGFAType | Facade Articulation Scheme